# VENTEX PRODUCT SPECIFICATION GUIDE                    FEBRUARY 2026

SECTION  23 37 20

# LOUVERS INTAKES AND VENTS

- GENERAL

  - SECTION INCLUDES

    - Prefinished wall louvres.

    - Additional support framing.

    - Bird screens.

    - Insect screens.

    - Blankoff Panels

  - RELATED REQUIREMENTS

    - Section 03 31 00 Structural Concrete – Adjacent wall and curb construction.

    - Section 04 20 00 Concrete Unit Masonry – Adjacent wall and curb construction.

    - Section 05 12 00 Structural Steel Framing – Connection to building structure.

    - Section 05 41 00 Structural Metal Stud Framing – Connection to building wall structure.

    - Section 07 25 13 Air and Vapour Membranes - Air/vapour barrier tie ins to insulated blankoff panels.

    - Section 07 92 00 Sealants – Sealing between louver frames and surrounding construction.

    - Section 08 44 00 Curtain Wall and Glazed Assemblies – Adjacent wall construction.

    - Section 23 30 00 HVAC Air Distribution - interface with plenum construction and control dampers.

  - REFERENCES

    - Abbreviations and Acronyms:

    - AMCA: Air Movement and Control Association International, Inc.; www.amca.org.

    - MSDS: Material Safety Data Sheets

    - PVDF: Polyvinylidene Fluoride

    - SMACNA- Sheet Metal and Air Conditioning Contractor’s National Association

  - REFERENCE STANDARDS:

    - AAMA 2605-05 - Voluntary Specification, Performance Requirements and Test Procedures for Superior Performance Organic Coatings on Aluminum Extrusions and Panels

    - AMCA 500-L - Laboratory Methods of Testing Louvers for Rating

    - AMCA 511 – Certified Ratings Program for Air Control Devices.4.

    - ASTM B209 (ASTM B209M) - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate

    - ASTMB221 Standard for Aluminum Alloy Extruded Bars, Rods, Wire, Profiles and Tubes

    - ASTM B244 - Standard Test Method for Measurement of Thickness of Anodic Coatings on Aluminum and of Other Nonconductive Coatings on Nonmagnetic Basis Metals with Eddy-Current Instruments

    - SMACNA - HVAC DUCT CONSTRUCTION STANDARDS 2020

    - ASTM E330-02 & 14 – Structural Uniform Load Performance Test

    - ASTM E331-00 – Water Resistance Test

    - ASTM E-283-04 – Air Leakage Test

  - SUBMITTALS

    - Product Data: For each type of product provide Printed catalog pages showing specified models with appropriate Air Movement and Control Association International (AMCA) Certified Ratings Seals.

    - Shop Drawings:

      - Submit Shop Drawings for work of this Section in accordance with Division 01. In addition to minimum requirements indicate following:

      - Structural supports and framing provided as part of this Section.

      - Clip angle connections and recommended anchor hardware.

      - Provision for structural and thermal movement between louvres and adjacent materials.

      - Show mullion profiles and locations weep paths, gaskets, flashing, sealant, and other means of preventing water intrusion,

      - Provision for structural and thermal movement between louvers and adjacent materials.

      - Indicate pressure drop, face area, and free area.

    - Employ a registered structural engineer specified herein is responsible for:

      - Production and review of Shop Drawings.

      - Stamping and signing each Shop Drawing and any associated calculations performed.

    - Samples:

      - Louvers minimum 600 mm (24") square.

      - Colour samples for each type of louver.

  - CLOSEOUT SUBMITTALS

    - Cleaning and Maintenance Manual.

    - Warranty

    - A copy of each shop drawing in its latest amended form.

  - QUALITY ASSURANCE

    - Source Limitations:

      - Obtain louvers and vents from single source from a single manufacturer where indicated to be of same type, design, or factory-applied color finish.

    - Sheet Metal and Air Conditioning Contractor’s National Association (SMACNA) Standard: Comply with recommendations in SMACNA's "Architectural Sheet Metal Manual" for fabrication, construction details, and installation procedures.

    - Qualifications:

      - Installers: Provide work of this Section executed by competent installers with minimum of 5 years experience in application of products, systems and assemblies specified and with approval and training of the product manufacturers.

      - Licensed Professionals: Employ a professional structural engineer carrying professional liability insurance and registered in the relevant jurisdiction in accordance with requirements of Division 01 to:

        - Design components of The Work of this Section requiring structural performance.

        - Be responsible for full assemblies and connections.

        - Be responsible for production and review of Shop Drawings.

        - Stamp and sign each Shop Drawing.

  - PROJECT CONDITIONS

    - Field Measurements: Verify actual dimensions of openings by field measurements before fabrication.

  - DELIVERY, STORAGE AND HANDLING

    - Delivery and Acceptance Requirements: Coordinate deliveries to comply with construction schedule and arrange for strategic off-the-ground, undercover storage locations.

    - Storage and Handling Requirements: Properly wrap louvres with protective coverings and put in suitable crates to prevent distortion and damage. Carefully unload, handle and store to prevent damage.

  - WARRANTY

    - Manufacturer Warranty: Warrant work of this Section against defects and/or deficiencies in accordance with General Conditions of the Contract.  Promptly correct any defects or deficiencies which become apparent within warranty period.

- PRODUCTS

  - MANUFACTURERS

    - Manufacturer List: Products of following manufacturers are acceptable subject to conformance to requirements of Drawings, Schedules and Specifications:

    - Ventex Inc., Alliston, Ontario, Canada - www.ventexinc.com

    - Substitution Limitations: Comparable Products from other manufacturers not listed herein may be accepted provided they meet requirements of this Specification after full review by Consultant before bidding closes.

  - PERFORMANCE DESIGN CRITERIA:

    - Design louver, screens and grilles in accordance with building code and to withstand live, dead, lateral, wind, seismic, handling, transportation and erection loads, imposed and other loads.

    - Provide for positive drainage to outside of any water entering joints and exterior face of system.

    - Louvers licensed to bear AMCA Certified Ratings Seal. Ratings based on tests and procedures performed in accordance with AMCA 511 and comply with AMCA Certified Ratings Program. AMCA Certified Ratings Seal applies to air performance and water penetration ratings.

    - Material thicknesses stated herein are a minimum. Be responsible for engineering calculations to ensure structural adequacy of wall louvres.

    - Structural Performance: Withstand the effects of gravity loads and the following loads and stresses within limits and under conditions indicated without permanent deformation of louvre components.

      - Deflection not greater than L/120 for louver blades between supports and L/180 for louver supports, without noise or metal fatigue caused by louver blade rattle or flutter, or permanent damage to fasteners and anchors.

      - Wind pressures shall be considered to act normal to the face of the building. Determine loads based on pressures indicated below:

        - Wind Loads: Design louvres to withstand maximum positive and negative wind loads in accordance with the latest building code based on fifty (50) year return period.

        - Seismic Loads in accordance with the latest building code.

    - Employ a registered structural engineer specified herein to:

      - Design components for work of this Section requiring structural performance.

      - Be responsible for determining sizes, joint spacing to allow thermal movement and loading of components in accordance with applicable codes and regulations.

    - Vibration Control: Louver members shall not vibrate when subjected to wind loading and/or adjacent to mechanical equipment.

    - Thermal Movements: Allow for thermal movements from ambient and surface temperature changes, without buckling, opening of joints, overstressing of components, failure of connections, or other detrimental effects.

      - Temperature Change (Range): 67°C (120°F), ambient; 100°C (180°F) material surfaces.

    - Frame and Blade Nominal Thickness:

      - Not less than 1.60 mm (0.063”) for blades and for frames unless otherwise indicated, to ASTM B221. Extruded aluminum alloy 6063-T6. Provide extruded aluminum blade supports in section modulus and depth to resist anticipated loads.

    - Mullion Type:

      - As indicated in the Drawings to ASTM B221. Extruded aluminum alloy 6063-T6.

  - MATERIALS

    - Aluminum Sheet: ASTM B209M, Alloy 3003 or 5005 with temper as required for forming, or as otherwise recommended by metal producer for required finish.

    - Fasteners: Use types and sizes to suit unit installation conditions.

      - Use Pan Head Robertson sheet metal screws for exposed fasteners unless otherwise indicated.

      - For colour-finished louvers, use fasteners with heads painted to match colour of louvers.

      - Anchoring Devices and Clips: Self Drilling and Tapping Screws with corrosion resistant coating, UCAN Ruspro, Buildex Climaseal 5 or similar approved coating.

      - Screw Anchors for Concrete and Masonry: Heavy Duty concrete anchor screws, Hilti Kwik HUS KH-EZ CRC carbon steel with mechanically galvanized coating or Heavy Duty Tapcon with Blue Climaseal rust resistant coating, Select fasteners to meet required loads using manufacturers technical guides.

    - Louver Supports:

      - Extruded Aluminum Supports: Angles or channels 6061 alloy aluminum to ASTM B221 standard.

      - Cold Formed Steel Supports: Galvanized Steel Structural Studs minimum .054” thick G90 Galvanized to 50,000psi.

    - Clip Angle Connections to Structure

      - Aluminum or galvanized steel clip angles for connection of louver frame and supports to adjacent structure designed to meet calculated loads.

  - MANUFACTURED UNITS

    - High Performance Blade Louver 50mm Deep

      - Basis of Design: Ventex Model 2210 (Channel Frame) / 2215 (Flange Frame).

      - Blade Type: Flat High Performance

        - Louvre Depth: 51 mm (2”).

      - Frame and blade thickness 1.60mm (.063”).

      - Free Area: 52.3% for louver size 1219 x 1219 (48” x 48”).

      - Free area velocity at the point of beginning water penetration not less than 491 FPM (2.49 m/s) (@0.01oz. /ft² of free area based on a 15 minute interval test).

      - Air Performance: Not more than 0.040” w.g. intake pressure drop at 697 fpm free-area velocity (Point of beginning water penetration

      - General Appearance

        - Provide mullions where indicated to meet wind load and deflection criteria or at a maximum of 900mm OC Where mullions are not indicated provide concealed vertical supports on interior side of louver to create a continuous blade appearance on the exterior

    - Accessories:

[Blank-off panels at mechanically inactive areas at heated interior locations. Not designed for attachment of control dampers]

      - Aluminum Insulated Blank-Off Panels: 51 mm (2 inch) thick, aluminum skin 1.0mm (.050”), mineral wool insulated core, factory installed with removable screws.

        - Finished to match louvers on exterior side.

[Blank-off panels at mechanically inactive areas at unheated interior spaces such as cold plenums or locations where wall insulation is located behind louvers such as parapets. Not designed for attachment of control dampers]

      - Aluminum Non Insulated Blank-Off Panels: Aluminum sheet 1.0mm (.050”) thick factory installed on to back of louver with removable screws.

        - Finished to match louvers on exterior side.

[Blank-off wall system at large louvers that are supplied in multiple stacked sections in width and height. Provides a continuous structural insulated wall behind louvers with pre-cut openings at intake and exhaust locations. Avoids open joints between louvered panel sections and at louver supports which occur with conventional blank-off panel systems]

      - Blank-off Wall System: Ventwall as manufactured by Ventex Inc. installed to structure prior to installation of louvers to provide a continuous uninterrupted insulated wall withstanding required loads and capable of supporting the louver system.

        - Structural system with interlocking panels 1067mm (42”) wide x 3048mm (120”) maximum height.

        - Inactive Panels:

        - 1.21mm (18 gauge), G90 galvanized steel construction with 100mm thick mineral wool core.

        - Active Panels:

        - 2.73mm (12 gauge) vertical channels and 1,21mm (18 gauge heads/sills, G90 galvanized steel construction.

        - Finished black powdercoat on exterior side

          - Optional Butyl tape seal at panel joints.

        - Optional Butyl tape seal at panel joints.

        - Installed prior to louvers acting as a continuous wall to meet wind loads transposed by louvers.

        - Air Leakage Resistance ASTM E283-04:

          - Maximum 0.65 l/s/m2 @ 75 Pa (0.13 cfm/ft2 @ 1.57 psf).

          - Maximum 1.20 l/s/m2 @ 266 Pa (.24 cfm/ft2 @ 5.56 psf)

        - Water Resistance ASTM E331-00:

          - No water infiltration 720 Pa (15.04 psf)

        - Structural Uniform Load Performance ASTN E330-02/14:

          - Maximum L/180 @ 3.360 Pa (45 psf)

        - Clip angles .25” thick hot dip galvanized steel for attachment of blankoff wall panels to steel structural girts.

    - Bird Screen:

      - Aluminum, 13 mm x 13 mm (1/2” x 1/2”) mesh, 1.6 mm (0.063”), intercrimped.

      - Frame: Extruded aluminum, removable.

    - Insect Screen:

      - Aluminum, 18 x 14 mesh

    - Sill Flashing: Formed aluminum, minimum nominal wall thickness 1.02 mm (0.040”).

      - Sill flashing to extend behind aluminum birdscreen on louvers without blankoff or to extend behind blank-off to drain water positively to exterior. Provide minimum 75mm (3”) upturn on interior edge.

    - Fabrication:

      - Assemble louvers in factory to minimize field splicing and assembly. Disassemble units as necessary for shipping and handling limitations. Clearly mark units for reassembly and coordinated installation.

      - Provide louver blades with extruded aluminum blade supports in section modulus and depth to resist loads anticipated and meet design requirements specified. Provide integral reinforcing ribs to prevent bowing and distortion.

      - Accurately cut and fit components to produce tight hairline junctures. Securely fasten frame members together with concealed fasteners

      - Fabricate bird screens using aluminum mesh securely enclosed by an extruded aluminum angle frame. Install bird screens on the inside of louvres and screw fasten to frames to permit removal if required.

  - FINISHES

    - General:  Where applicable comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

    - Appearance of Finished Work: Noticeable variations within a distance of 3048mm (120”) are not acceptable. Variations in appearance of abutting or adjacent pieces are acceptable if they are within one-half of the range of approved samples. Variations in appearance of other components are acceptable if they are within the range of approved samples and are assembled or installed to minimize contrast.

    - Superior & High Performance Organic Paint Finish Materials – Extrusion Coatings

      - Liquid Fluoropolymer Aluminum Extrusion Coatings, AAMA 2605: Minimum 70% PVDF resin, by weight, in color coat and clear topcoat.

[Choose between Two Coat or Three Coat System. Three coat systems are required for colours utilizing metallic flake. If colour is unknown it is recommended to specify a 3 coat system for tendering purposes]

        - Two Coat System - PPG Duranar, Duranar Sunstorm, Sherwin Williams Fluropon

          - Dry Film Thickness, ASTM D 7091: 0.20 mil primer coat plus 1.0 mil color coat, 1.20 mil total, minimum thickness

        - Three Coat System PPG Duranar XL, Sherwin Williams Fluropon

          - Dry Film Thickness, ASTM D 7091: 0.20 mil primer coat plus, 1.0 mil color coat and 0.4 mil clear topcoat, 1.6 mil total minimum thickness

      - Acrylic Enamel Finish: Liquid acrylic finishes meeting AAMA 2603

        - PPG Duracron

          - Dry Film Thickness, ASTM D 7091: 1.0 mil +/- 0.2 mil.

    - Anodic Finishes:

[Choose type of anodized finish. Clear anodized finishes are available in two thicknesses. NAAMM recommends Class 1 for all exterior applications and states that Class 2 is acceptable for exterior applications where cleaning can be done periodically. However Class 2 is in fact widely used in all exterior applications where salt air or in highly corrosive environments.

      - Clear Anodized Finish

        - [Clear Anodized Class 1 – AA-M12C22A41 minimum thickness .0007” (18 microns)]

        - [Clear Anodized Class 2 – AA-M12C22A31 minimum thickness .0004” (10 microns)]

      - [Bronze Anodized Finish]

      - [Champagne Bronze Anodized Class 1 – AA-M12C22A44 .0007” (18 microns)]

      - [Light Bronze Anodized Class 1 – AA-M12C22A44 .0007” (18 microns)]

      - [Medium Bronze Anodized Class 1 – AA-M12C22A44 .0007” (18 microns)]

      - [Dark Bronze Anodized Class 1 – AA-M12C22A44 .0007” (18 microns)]

      - [Black Anodized Class 1 – AA-M12C22A44 .0007” (18 microns)]

- EXECUTION

  - EXAMINATION

    - Verification of Conditions: Verify actual site dimensions and location of adjacent materials prior to commencing work. Notify Consultant in writing of any conditions which would be detrimental to the installation.

    - Evaluation and Assessment: Commencement of work implies acceptance of previously completed work.

    - Proceed with installation only after unsatisfactory conditions have been corrected.

  - PREPARATION

    - Coordinate setting drawings, diagrams, templates, instructions, and directions for installation of anchorages that are to be embedded in concrete or masonry construction. Coordinate delivery of such items to project site.

  - INSTALLATION

    - Locate and place louvers and vents level, plumb, and at indicated alignment with adjacent Work.

    - Use concealed anchorages where possible. Provide brass or lead washers fitted to screws where required to protect metal surfaces and to make a weathertight connection.

    - Secure angle reinforcing as an integral part of the assembly. Neatly miter and weld corners at areas indicated.

    - Cut and fit components to produce tight hairline junctures. Securely fasten frame members together with concealed welds and seal with sealant to ensure watertight joints.

    - Provide perimeter reveals and openings of uniform width for sealants and joint fillers, as indicated.

    - Repair finishes damaged by cutting, welding, soldering, and grinding. Restore finishes so no evidence remains of corrective work. Return items that cannot be refinished in the field to the factory, make required alterations, and refinish entire unit or provide new units.

    - Protect unpainted galvanized and non-ferrous metal surfaces that will be in contact with concrete, masonry, or dissimilar metals from corrosion and galvanic action by applying a heavy coating of bituminous paint or by separating surfaces with waterproof gaskets. tape or nonmetallic flashing.

    - Secure support frames to openings. Install louvers plumb or true to slope and at correct location in openings, with bird screens on inside. Method of attachment shall be concealed.

    - Install concealed gaskets, flashings, joint fillers, and insulation as louver installation progresses. Comply with Section 07 92 00 “Joint Sealants" for sealants applied during louver installation.

    - Apply sealant to perimeter of frames to adjacent materials or to supports using joint backing and sealant. Neatly tool and finish joints.

  - SITE QUALITY CONTROL

    - Non-Conforming Work: Replace damaged work which cannot be satisfactorily repaired, restored or cleaned, to satisfaction of Consultant at no cost to Owner.

    - Manufacturer Services: Arrange for product manufacturer’s technical representative to:

      - Meet and discuss installation procedures and unique conditions at the place of the work.

      - Inspect substrate surfaces and recommend solutions to accommodate adverse conditions.

      - Periodically visit and inspect installation and report unsatisfactory conditions.

      - Attend final inspection and to submit written certification that products, systems and assemblies have been installed in accordance with manufacturer’s requirements.

  - CLEANING

    - Clean exposed surfaces of louvres and vents that are not protected by temporary covering, to remove fingerprints and soil during construction period. Do not let soil accumulate during construction period.

    - Before final inspection, clean exposed surfaces with water and a mild soap or detergent not harmful to finishes. Thoroughly rinse surfaces and dry.

    - Restore louvers and vents damaged during installation and construction so no evidence remains of corrective work. If results of restoration are unsuccessful, as determined by Consultant, remove damaged units and replace with new units.

    - Touch up minor abrasions in factory applied finishes with air-dried coating that matches color and gloss of, and is compatible with, factory-applied finish coating.

    - Demonstrate proper cleaning methods to Owner. Prepare a "Cleaning and Maintenance Manual" listing types of cleaning compounds and cleaning methods.

  - END OF SECTION