## Data input and results
UNIVERSAL LOUVRE SELECTION
PROJECT:
DATE: |  |  |  | BY:
INPUT DATA:
Louvre type |  |  | Material
Please Note: Medium Louvre does not come in stainless steel as standard
|  |  | Mullion spacing |  |  |  | m
Accessories |  |  | Mullion type at ends
Direction of air flow |  |  | Steelwork |  | 1UL |  | m
|  |  | spacing |  | 2UL |  | m
Connections |  |  |  |  | 3UL |  | m
Air flow rate |  | m3/s | Steelwork thickness |  |  |  | m
Other equipment in series |  |  | Ambient air density |  |  |  | kg/m3
Maximum air pressure drop |  | Pa
Fill in 2 out of 3
Maximum louvre height |  | m | Leave 3rd blank
Maximum louvre width |  | m
RESULTS |  | Option 1 |  |  | Option 2
Selected louvre type |  | N/A |  |  | N/A
HEVAC classification |  | N/A |  |  | N/A
Pressure drop |  | N/A | Pa |  | N/A | Pa
Core velocity |  | N/A | m/s |  | N/A | m/s
Panel height |  | N/A | m |  | N/A | m
Panel width |  | N/A | m |  | N/A | m
Panel weight |  | N/A | kg |  | N/A | kg
Notes:
© Colt International Limited 2024 | [5 empty] | v1.4 May 2024

## information
1 | The program combines the existing Colt programs 'ulpress' and 'ulpanel' with a new front end.
The results will not be the same as the old programs since the opportunity was taken to update some data.
2 | Louvre codes take the form 1UL/S where the first number is the number of louvre banks (1, 2 or 3)
and the final letter denotes whether the lovre is shallow section 50mm pitch (S) or deep section 100mm pitch (D).
3 | The louvre performance data is taken from BSRIA report number 55130/1 dated December 1988.
4 | Louvre air flow performance was measured with birdguard fitted.
Percent change in Cv is taken as:
|  | No b.g. | With i.m.
| 1UL | 7 | -6
| 2UL | 4 | -4
| 3UL | 3 | -3
5 | The louvre weights are calculated using the formulae in Colt GPTS 1200.
They exclude any support steelwork.
6 | The classifications for 'location' are taken from CIBSE Guide A, 3.3.9.4
sheltered is up to 3rd floor in city centres
normal is 4th to 8th floors in city centres and most rural and suburban buildings
severe is 9th floor and above in city centres, floors above 5th in rural and suburban areas and coastal and hill sites.
7 | Steelwork spacing should be as calculated from the design charts in GPTS 1200 or Colt leaflets.
The default values used are typical values for' normal' locations.
8 | Classifications are taken from BS EN 13030 (formerly the HEVAC test method).
A = 99% rainfall rejection or better
B = 95% to 98.99% rainfall rejection
C = 80% to 94.99% rainfall rejection
D = less than 80% rainfall rejection
1 = Airflow coefficient (Cv) of 0.4 or better
2 = Airflow coefficient (Cv) of 0.3 to 0.399
3 = Airflow coeficient (Cv) of 0.2 to 0.299
4 = Airflow coefficient (Cv) of less than 0.2
9 | Core velocity is the nominal velocity through the louvre panel ignoring the blockage effect of the louvres themselves.
10 | Where other equipment in series is selected the program assumes a useful throat area equivalent to the louvre core area.
This is intended to provide a conservative selection.
11 | This program was written by Paul Compton.
12 | The easiest way to copy into Word for a report is to highlight and copy, then go to the Word document and click on
edit, paste special, picture. The text is not editable but is correctly laid out and can be moved and resized.
Amendment record
2003-06-01 |  | Issued as draft for comment version 1.0dev
2003-07-01 |  | Issued as second draft incorporating comments version 1.a dev
2003-11-01 |  | Correction made to height in ulpress and issued as version 1.0a
2004-03-01 |  | Correction made to selection of louvre type to make more robust and issued as version 1.1
2009-05-01 |  | Addition of option to add other equipment in series and issued as version 1.2
2009-12-01 |  | Modification to louvre choice if number of banks not selected and issued as version 1.2a
2010-06-01 |  | Warning added when number of banks not specified if core velocity exceeds 3.5m/s and issued as 1.2b
2013-05-01 |  | Correction made to selection of height or width and issued as 1.2c
2016-10-01 |  | Reviewed and tidied up with no technical changes and issued as 1.2d
2023-12-01 |  | Corrections to multiple lookups on the selection tab and addition of the 1UL/M option. Issued as version 1.3
2024-05-01 |  | Addition of the acoustic section and handling notes on the selection page. Issued as version 1.4

## Acoustics (hidden)
Unit | Mullion Centres | Direction | Mullions | Face Speed (m/s) | [12 empty] | Unit | Mullion Centres | Direction | Mullions | Face Speed (m/s) | [12 empty] | Unit | Mullion Centres | Direction | Mullions | Face Speed (m/s)
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1UL/S | 600 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 2UL/S | 600 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3UL/S | 600 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5 |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 4 |  |  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 21 |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 800 | Inlet | Half | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 38 |  | 800 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 800 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 |  |  |  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1000 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1000 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  | 1000 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Extract | Half | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 |  |  |  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 |  |  |  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1250 | Inlet | Half | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1250 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1250 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 1 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Extract | Half | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1UL/M | 600 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2UL/D | 600 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3UL/D | 600 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Extract | Half | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  |  |  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 800 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 800 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 800 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Extract | Half | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 |  |  |  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1000 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1000 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1000 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Extract | Half | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 |  |  |  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1250 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  |  | 1250 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1250 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Extract | Half | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1UL/D | 600 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Unit Row | Centre Row Add | Direction Row Add | Mull Row Add |  |  | Final Row |  | Unit Col |  | Speed Col Add |  |  | Final Col |  | Final Cell | Vibration |  | Core Vel Err
|  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [22 empty] | NA corrected
|  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 | N/A | #VALUE! | 8 | 0 | 0 |  |  | #VALUE! |  | #VALUE! |  | 12 |  |  | #VALUE! |  | #VALUE! | FALSE |  | FALSE
| 800 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 | N/A | #VALUE! | 8 | 0 | 0 |  |  | #VALUE! |  | #VALUE! |  | 12 |  |  | #VALUE! |  | #VALUE! | FALSE |  | FALSE
|  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Key | 0 | No Noise |  |  | Option 1 |  |  |  | Option 2 | [7 empty] | FALSE
|  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | Noise
| 1000 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1250 | Inlet | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Extract | Half | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## selection (hidden)
Table of choices
[9 empty] | al | al | ss | ss | gs | gs | Chosen from table choice 1 |  | wres
Choice from table: | choice 1 | #N/A | [5 empty] | 1UL/D | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | Critical | important | Unimportant
| choice 2 | #N/A | [5 empty] | 1UL/M | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | loc | Exposed | 3UL | 3UL | 1UL
|  |  |  | core velocity |  |  | weight | 1UL/S | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Normal | 3UL | 2UL | 1UL
Louvre type: | choice 1 | N/A |  | 0 |  |  |  | 2UL/D | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Sheltered | 3UL | 2UL | 1UL
| choice 2 | N/A |  | 0 | PDROP |  |  | 2UL/S | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 2 | 3 | 4
| choice 2* | N/A |  | 0 |  |  |  | 3UL/D | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[8 empty] | 3UL/S | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Chosen from table choice 1 |  | wres
|  | 0 | [14 empty] | Critical | Important | Unimportant
[15 empty] | loc | Exposed | N/A | 2UL | N/A
RESULTS |  |  | Option 1 |  | Option 2 | [10 empty] | Normal | 2UL | N/A | N/A
|  |  | (Best weather protection) |  | (Best air flow performance) |  |  | Notes | [7 empty] | Sheltered | 2UL | N/A | N/A
Selected louvre type |  |  | N/A |  | N/A |  | 1 | [9 empty] | 2 | 3 | 4
2
HEVAC classification |  |  | N/A |  | N/A |  | 3
[7 empty] | 4 | [7 empty] | louvre type |  | 1UL | 2UL | 3UL | N/A
Pressure drop |  |  | N/A | Pa | N/A | Pa | 5 | [7 empty] | Type | N/A | N/A | N/A | N/A | N/A
[7 empty] | 6 | [8 empty] | UL/S | 1UL/S | 2UL/S | 3UL/S | N/A
Core Velocity |  |  | N/A | m/s | N/A | m/s | [9 empty] | UL/M | 1UL/M | 1UL/M | 1UL/M | N/A
[8 empty] | Note Index | [7 empty] | UL/D | 1UL/D | 2UL/D | 3UL/D | N/A
Panel height |  |  | N/A | m | N/A | m | [10 empty] | 2 | 3 | 4 | 5
[10 empty] | Notes Count |  | 0
Panel width |  |  | N/A | m | N/A | m | [8 empty] | Hevac Classifications
Air Flow Speed (m/s)
Percentage free area |  |  | N/A |  | N/A |  | * | [8 empty] | 0 | 1 | 2.2 | 3.5
[15 empty] | 1UL/S | D1 | D1 | D1 | D1 | 2
Measured free area |  |  | N/A | m2 | N/A | m2 | [8 empty] | 1UL/M | D1 | D1 | D1 | D1 | 3
[8 empty] | Notes Blanks Removed | [6 empty] | 1UL.D | D1 | D1 | D1 | D1 | 4
Weight |  |  | N/A | kg | N/A | kg | [8 empty] | 2UL/S | A2 | B2 | C2 | D2 | 5
[15 empty] | 2UL/D | A2 | B2 | C2 | D2 | 6
[15 empty] | 3UL/S | A3 | A3 | A3 | A3 | 7
[15 empty] | 3UL/D | A3 | A3 | A3 | A3 | 8
The notes section collates all the different notes
The Notes Index section gives the index of the valid notes and the total note count
The Notes Blanks Removed section removes any blank notes

## ulpanel (hidden)
Calculations:
if height entered....
[10 empty] | zeta | accfac | cvel | carea | cwidth | nummull | oawid
Colt Universal Louvre Systems | [8 empty] | 1 | 5.2847 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1UL/S | zeta = k
Calculation of Panel Size if Flowrate and Maximum Pressure Drop are known | [8 empty] | 2 | 6.9252 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[9 empty] | 3 | 4.2847 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[9 empty] | 4 | 6.4252 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Input Data: | [8 empty] | 5 | 4.8839 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1UL/M
[9 empty] | 6 | 5.6689 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Volume flow rate: | [5 empty] | 0 | m3/s |  | 7 | 3.8839 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Maximum Pressure Drop: | [5 empty] | 0 | Pa |  | 8 | 5.1689 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Mullion spacing: | [5 empty] | 1 | m |  | 9 | 4.53 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1UL/D
Site ambient air density: | [5 empty] | 1.2 | kg/m3 |  | 10 | 4.72 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[9 empty] | 11 | 3.53 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[9 empty] | 12 | 4.22 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Limiting Dimension: |  |  |  |  | h or w | w |  |  | 13 | 10.54 | 0.96 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2UL/S
(h = height, w = width) |  |  |  |  | value | 0 | m |  | 14 | 16 | 0.96 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[5 empty] | 1UL | 2UL | 3UL |  | 15 | 9.54 | 0.96 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Thickness of horizontal steelwork: |  |  |  |  | 0.1 | 0.1 | 0.1 | m | 16 | 15.5 | 0.96 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Spacing of horizontal steelwork: |  |  |  |  | 1.25 | 2 | 3.2 | m | 17 | 14.79 | 0.96 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2UL/D
Calculations: | [8 empty] | 18 | 16 | 0.96 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | Width (m) | Height (m) |  | Value for selection |  | cvel | 19 | 13.79 | 0.96 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[9 empty] | 20 | 15.5 | 0.96 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1UL/SH: |  | inlet | 0 | #DIV/0! |  | 1UL/D | #DIV/0! | 0 | 21 | 13.03 | 0.97 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3UL/S
|  | exhaust | 0 | #DIV/0! |  | 1UL/M | #DIV/0! | 0 | 22 | 20.66 | 0.97 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1UL/MH: |  | inlet | 0 | #DIV/0! |  | 1UL/S | #DIV/0! | 0 | 23 | 12.03 | 0.97 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | exhaust | 0 | #DIV/0! |  | 2UL/D | #DIV/0! | 0 | 24 | 20.16 | 0.97 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1UL/DH: |  | inlet | 0 | #DIV/0! |  | 2UL/S | #DIV/0! | 0 | 25 | 16 | 0.97 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3UL/D
|  | exhaust | 0 | #DIV/0! |  | 3UL/D | #DIV/0! | 0 | 26 | 20.66 | 0.97 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2UL/SH: |  | inlet | 0 | #DIV/0! |  | 3UL/S | #DIV/0! | 0 | 27 | 15 | 0.97 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | exhaust | 0 | #DIV/0! |  |  |  |  | 28 | 20.16 | 0.97 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2UL/DH: |  | inlet | 0 | #DIV/0!
|  | exhaust | 0 | #DIV/0! | [5 empty] | if width entered....
3UL/SH: |  | inlet | 0 | #DIV/0! | [5 empty] | nummull | cwidth | cheight | oaht
|  | exhaust | 0 | #DIV/0! |  |  |  |  | 1 | 0 | -0.18 | #DIV/0! | #DIV/0! | 1UL/S
3UL/DH: |  | inlet | 0 | #DIV/0! |  |  |  |  | 2 | 0 | -0.18 | #DIV/0! | #DIV/0!
|  | exhaust | 0 | #DIV/0! |  |  |  |  | 3 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 4 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 5 | 0 | -0.18 | #DIV/0! | #DIV/0! | 1UL/M
[9 empty] | 6 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 7 | 0 | -0.18 | #DIV/0! | #DIV/0!
Notes: | [8 empty] | 8 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 9 | 0 | -0.18 | #DIV/0! | #DIV/0! | 1UL/H
a) Pressure drops are based upon the following values of Cv: | [8 empty] | 10 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 11 | 0 | -0.18 | #DIV/0! | #DIV/0!
| Inlet | Extract |  | Inlet | Extract |  | Inlet | Extract | 12 | 0 | -0.18 | #DIV/0! | #DIV/0!
1UL/SH: | 0.435 | 0.38 | 2UL/SH: | 0.308 | 0.25 | 3UL/SH: | 0.277 | 0.22 | 13 | 0 | -0.18 | #DIV/0! | #DIV/0! | 2UL/S
1UL/MH: | 0.4525 | 0.42 | [6 empty] | 14 | 0 | -0.18 | #DIV/0! | #DIV/0!
1UL/DH: | 0.47 | 0.46 | 2UL/DH: | 0.26 | 0.25 | 3UL/DH: | 0.25 | 0.22 | 15 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 16 | 0 | -0.18 | #DIV/0! | #DIV/0!
And K | [8 empty] | 17 | 0 | -0.18 | #DIV/0! | #DIV/0! | 2UL/D
| Inlet | Extract |  | Inlet | Extract |  | Inlet | Extract | 18 | 0 | -0.18 | #DIV/0! | #DIV/0!
1UL/SH: | 5.2847 | 6.9252 | 2UL/SH: | 10.5414 | 16 | 3UL/SH: | 13.0329 | 20.6612 | 19 | 0 | -0.18 | #DIV/0! | #DIV/0!
1UL/MH: | 4.8839 | 5.6689 | [6 empty] | 20 | 0 | -0.18 | #DIV/0! | #DIV/0!
1UL/DH: | 4.5269 | 4.7259 | 2UL/DH: | 14.7929 | 16 | 3UL/DH: | 16 | 20.6612 | 21 | 0 | -0.18 | #DIV/0! | #DIV/0! | 3UL/S
[9 empty] | 22 | 0 | -0.18 | #DIV/0! | #DIV/0!
NOTE: | 1UL/MH has not been indepently tested, these values are only meant for very rough estimation | [7 empty] | 23 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 24 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 25 | 0 | -0.18 | #DIV/0! | #DIV/0! | 3UL/D
[9 empty] | 26 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 27 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 28 | 0 | -0.18 | #DIV/0! | #DIV/0!

## ulpress (hidden)
Calculations:
[10 empty] | k | mod for BG
[10 empty] | zeta | accfac | nummull | cwidth | cheight | carea | cvel
Colt Universal Louvre Systems | [8 empty] | 1 | 5.2847 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0 | 1UL/S
Calculation of Pressure Drop if Flowrate and Panel Size are known | [8 empty] | 2 | 6.9252 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0
(Louvre panels fitted with birdguard) | [8 empty] | 3 | 4.2847 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0
[9 empty] | 4 | 6.4252 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0
Input Data: | [8 empty] | 5 | 4.8839 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0 | 1UL/M
[9 empty] | 6 | 5.6689 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0
Volume flow rate: | [5 empty] | 0 | m3/s |  | 7 | 3.8839 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0
Total panel width: | [5 empty] | 0 | m |  | 8 | 5.1689 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0
Mullion spacing: | [5 empty] | 1 | m |  | 9 | 4.5269 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0 | 1UL/D
Total panel height: | [5 empty] | 0 | m |  | 10 | 4.7259 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0
[5 empty] | 1UL | 2UL | 3UL |  | 11 | 3.5269 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0
Thickness of intermediate steelwork: |  |  |  |  | 0.1 | 0.1 | 0.1 | m | 12 | 4.2259 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0
Spacing of intermediate steelwork: |  |  |  |  | 1.25 | 2 | 3.2 | m | 13 | 10.5414 | 0.96 | 0 | -0.18 | -0.08 | 0.0144 | 0 | 2UL/S
Site ambient air density: | [5 empty] | 1.2 | kg/m3 |  | 14 | 16 | 0.96 | 0 | -0.18 | -0.08 | 0.0144 | 0
[9 empty] | 15 | 9.5414 | 0.96 | 0 | -0.18 | -0.08 | 0.0144 | 0
[9 empty] | 16 | 15.5 | 0.96 | 0 | -0.18 | -0.08 | 0.0144 | 0
[9 empty] | 17 | 14.7929 | 0.96 | 0 | -0.18 | -0.08 | 0.0144 | 0 | 2UL/D
[9 empty] | 18 | 16 | 0.96 | 0 | -0.18 | -0.08 | 0.0144 | 0
Calculations: | [8 empty] | 19 | 13.7929 | 0.96 | 0 | -0.18 | -0.08 | 0.0144 | 0
[9 empty] | 20 | 15.5 | 0.96 | 0 | -0.18 | -0.08 | 0.0144 | 0
Pressure Drop: |  | Inlet | Extract |  | Value for selection |  | cvel |  | 21 | 13.0329 | 0.97 | 0 | -0.18 | -0.08 | 0.0144 | 0 | 3UL/S
[9 empty] | 22 | 20.6612 | 0.97 | 0 | -0.18 | -0.08 | 0.0144 | 0
| 1UL/D | 0 | 0 | Pa | 0 | Pa | 0 |  | 23 | 12.0329 | 0.97 | 0 | -0.18 | -0.08 | 0.0144 | 0
| 1UL/M | 0 | 0 | Pa | 0 | Pa | 0 |  | 24 | 20.1612 | 0.97 | 0 | -0.18 | -0.08 | 0.0144 | 0
| 1UL/S | 0 | 0 | Pa | 0 | Pa | 0 |  | 25 | 16 | 0.97 | 0 | -0.18 | -0.08 | 0.0144 | 0 | 3UL/D
| 2UL/D | 0 | 0 | Pa | 0 | Pa | 0 |  | 26 | 20.6612 | 0.97 | 0 | -0.18 | -0.08 | 0.0144 | 0
| 2UL/S | 0 | 0 | Pa | 0 | Pa | 0 |  | 27 | 15 | 0.97 | 0 | -0.18 | -0.08 | 0.0144 | 0
| 3UL/D | 0 | 0 | Pa | 0 | Pa | 0 |  | 28 | 20.1612 | 0.97 | 0 | -0.18 | -0.08 | 0.0144 | 0
| 3UL/S | 0 | 0 | Pa | 0 | Pa | 0
Notes:
a) Pressure drops are based upon the following values of Cv:
| Inlet | Extract |  | Inlet | Extract |  | Inlet | Extract
1UL/SH: | 0.435 | 0.38 | 2UL/SH: | 0.308 | 0.25 | 3UL/SH: | 0.277 | 0.22
1UL/MH: | 0.4525 | 0.42
1UL/DH: | 0.47 | 0.46 | 2UL/DH: | 0.26 | 0.25 | 3UL/DH: | 0.25 | 0.22
And K
| Inlet | Extract |  | Inlet | Extract |  | Inlet | Extract
1UL/SH: | 5.2847 | 6.9252 | 2UL/SH: | 10.5414 | 16 | 3UL/SH: | 13.0329 | 20.6612
1UL/MH: | 4.8839 | 5.6689
1UL/DH: | 4.5269 | 4.7259 | 2UL/DH: | 14.7929 | 16 | 3UL/DH: | 16 | 20.6612
NOTE: | 1UL/MH has not been indepently tested, these values are only meant for very rough estimation