## Blad2
Product: |  |  | MODBUS TCP REGISTERS IN SX:UNO (021) FOR PRESSURE REGULATION
8SC2-1:021
SX:UNO/DUO - Status Register
Address 0-base | Register 1-base | Modicon notation reg.read | Read reg func code | Write reg func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit nr. | Modicon notation bit read | Read bit func code | Write bit func code | Function | Action/remarks
32 | 33 | 4x0033 | 3 | N/A | 0x0001 | 0 | 1 | 513 | 0x0513 | 1 | N/A | Standby bit (1=Standby)
32 | 33 | 4x0033 | 3 | N/A | 0x0002 | 1 | 2 | 514 | 0x0514 | 1 | N/A | Fire state | Dampers closed (external/internal cause)
32 | 33 | 4x0033 | 3 | N/A | 0x0004 | 2 | 3 | 515 | 0x0515 | 1 | N/A | Smoke detector Loop error | Previous loop error
32 | 33 | 4x0033 | 3 | N/A | 0x0008 | 3 | 4 | 516 | 0x0516 | 1 | N/A | Damper 1 error
32 | 33 | 4x0033 | 3 | N/A | 0x0010 | 4 | 5 | 517 | 0x0517 | 1 | N/A | Function test state | Set while the local damper(s) exercise
32 | 33 | 4x0033 | 3 | N/A | 0x0020 | 5 | 6 | 518 | 0x0518 | 1 | N/A | Damper 2 error | Modules with two dampers, not SX:UNO
32 | 33 | 4x0033 | 3 | N/A | 0x0040 | 6 | 7 | 519 | 0x0519 | 1 | N/A | Dampers sum error
32 | 33 | 4x0033 | 3 | N/A | 0x0080 | 7 | 8 | 520 | 0x0520 | 1 | N/A | Not used | Bit always cleared
32 | 33 | 4x0033 | 3 | N/A | 0x0100 | 8 | 9 | 521 | 0x0521 | 1 | N/A | Damper 1 closed
32 | 33 | 4x0033 | 3 | N/A | 0x0200 | 9 | 10 | 522 | 0x0522 | 1 | N/A | Damper 1 open
32 | 33 | 4x0033 | 3 | N/A | 0x0400 | 10 | 11 | 523 | 0x0523 | 1 | N/A | Damper 2 closed | Modules with two dampers, not SX:UNO
32 | 33 | 4x0033 | 3 | N/A | 0x0800 | 11 | 12 | 524 | 0x0524 | 1 | N/A | Damper 2 open | Modules with two dampers, not SX:UNO
32 | 33 | 4x0033 | 3 | N/A | 0x1000 | 12 | 13 | 525 | 0x0525 | 1 | N/A | Smoke detector normal run
32 | 33 | 4x0033 | 3 | N/A | 0x2000 | 13 | 14 | 526 | 0x0526 | 1 | N/A | Local alarm point state | Local fire (smoke detector)
32 | 33 | 4x0033 | 3 | N/A | 0x4000 | 14 | 15 | 527 | 0x0527 | 1 | N/A | Smoke detector service alarm | Clean the detector
32 | 33 | 4x0033 | 3 | N/A | 0x8000 | 15 | 16 | 528 | 0x0528 | 1 | N/A | Smoke loop broken | Local smoke detector loop broken. Also sets local fire alarm (bit 526)
SX:UNO/DUO - Command Register
Address 0-base | Register 1-base | Modicon notation reg.read/write | Read reg func code | Write reg func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit nr. | Modicon notation bit read | Read bit func code | Write bit func code | Function | Action/remarks
44 | 45 | 4x0045 | 3 | 6 | 0x0001 | 0 | 1 | 705 | 0x0705 | 1 | 5 | Forced damper opening | Selective smoke exhaust, force damper opening during fire alarm
44 | 45 | 4x0045 | 3 | 6 | 0x0002 | 1 | 2 | 706 | 0x0706 | 1 | 5 | External fire alarm | External fire damper will close
44 | 45 | 4x0045 | 3 | 6 | 0x0004 | 2 | 3 | 707 | 0x0707 | 1 | 5 | Reset local alarms (smoke detector) | Automatically cleared
44 | 45 | 4x0045 | 3 | 6 | 0x0008 | 3 | 4 | 708 | 0x0708 | 1 | 5 | Close damper | E.g. for night operation
44 | 45 | 4x0045 | 3 | 6 | 0x0010 | 4 | 5 | 709 | 0x0709 | 1 | 5 | Function test / Exercise | Automatically cleared
Note: Write only once when a command is issued and not continuously (Reset local alarms / Function test).
SX:UNO/DUO - Additional Registers
Address 0-base | Register 1-base | Modicon notation reg.read/write | Read reg func code | Write reg func code | Default value | Function |  |  | Action/remarks
32771 | 32772 | 4x32772 | 3 | 6 | 25 | Watchdog time/inputs debounce |  |  | Debounce 100ms and no watchdog at delivery. Calculation formula: Wtime(seconds) * 256 + 25 Note:max 255 seconds
32780 | 32781 | 4x32781 | 3 | 6 | 400 | Smoke detector loop level |  |  | Below=loop error=fire. 400=4mA
32781 | 32782 | 4x32782 | 3 | 6 | 1600 | Smoke detector service lev. |  |  | Above=Service request. 1600=16mA
32782 | 32783 | 4x32783 | 3 | 6 | 3000 | Smoke detector smoke lev. |  |  | Above=Fire. 3000=30mA
32822 | 32823 | 4X32823 | 3 | 6 | 0 | Int. pressure sensor zero offset |  |  | Zero offset adjustment for optional internal pressure sensor |  |  |  | Preferably use the dff-form to configure the offset
32823 | 32824 | 4x32824 | 3 | 6 | 4096 | Int. pressure sensor gain |  |  | Gain adjustment for optional internal pressure sensor. 4096=100% |  |  |  | Preferably use the dff-form to configure the gain
32819 | 32820 | 4x32820 | 3 | 6 | 0 | Ext. pressure sensor 0V pressure |  |  | Pa. External pressure sensor pressure at 0 volt input |  |  |  | Preferably use the dff-form to configure the setting
32820 | 32821 | 4x32821 | 3 | 6 | 1000 | Ext. pressure sensor 10V pressure |  |  | Pa. External pressure sensor pressure at 10 volt input |  |  |  | Preferably use the dff-form to configure the setting
53 | 54 | 4x0054 | 3 | N/A |  | Pressure, current value |  |  | Pa. Read only RAM
32826 | 32827 | 4x32827 | 3 | 6 | 100 | Pressure setpoint (EEPROM) |  |  | Pa. Initial setpoint value (until it may be overwritten by controlling system) |  |  |  | Preferably use the dff-form to configure the initial Pressure setpoint
58 | 59 | 4x0059 | 3 | 6 | 100 | Pressure setpoint (RAM) |  |  | Pa. Will hold the initial setpoint value above until it may be overwritten |  |  |  | Often changing setpoint values should be written to this register
32838 | 32839 | 4x32839 | 3 | 6 | 100 | P-Band (EEPROM) |  |  | Pa. Range 20-400 Pa |  |  |  | Preferably use the dff-form to configure the Proportional Band
70 | 71 | 4x0071 | 3 | 6 | 100 | P-Band (RAM) |  |  | Pa. Range 20-400 Pa
32829 | 32830 | 4x32830 | 3 | 6 | 600 | Integration Time (EEPROM) |  |  | Seconds |  |  |  | Preferably use the dff-form to configure the Integration Time
61 | 62 | 4x0062 | 3 | 6 | 600 | Integration Time (RAM) |  |  | Seconds
32794 | 32795 | 4x32795 | 3 | 6 | 0 | Min Damper Opening |  |  | Min opening. 0-4096=0-10V=0-100% |  |  |  | Preferably use the dff-form to configure the Min Damper Opening
32796 | 32797 | 4x32797 | 3 | 6 | 4096 | Max Damper Opening |  |  | Max opening. 0-4096=0-10V=0-100% |  |  |  | Preferably use the dff-form to configure the Max Damper Opening
41 | 42 | 4x0042 | 3 | N/A | N/A | Time left to exercise |  |  | Hours left before exercise. Read only RAM
32803 | 32804 | 4x32804 | 3 | 6 | 48 | Exercise interval |  |  | Hours between exercise. 0=No automatic function test
32804 | 32805 | 4x32805 | 3 | 6 | 640 | Damper closing time |  |  | Max closing time (unit 1/16s). Default 40s
32810 | 32811 | 4x32811 | 3 | 6 | 2880 | Damper opening time |  |  | Max opening time (unit 1/16s). Default 180s
6 | 7 | 4x0007 | 3 | 6 | 4096 | Damper position |  |  | 0-4096=0-10V=0-100% open
Note: Modbus registers 32xxx are stored in EEPROM (non-volatile memory). Do not write continuously to these, since each register is limited to maximum 1 million writes.
Introduced in PLC version 1.3 pressure setpoint is initially 100 Pa factory default so if power is applied without any pressure sensor connected, then the unit will try to open the damper.