## Blad2
Product: |  |  | MODBUS TCP REGISTERS IN SX:UNO AND SX:DUO
8SC2-1:004 (SX:UNO)
8SC2:004 (SX:DUO)
SX:UNO/DUO - Status Register
Address 0-base | Register 1-base | Modicon notation reg.read | Read reg func code | Write reg func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit nr. | Modicon notation bit read | Read bit func code | Write bit func code | Function | Action/remarks
32 | 33 | 4x0033 | 3 | N/A | 0x0001 | 0 | 1 | 513 | 0x0513 | 1 | N/A | Standby bit (1=Standby)
32 | 33 | 4x0033 | 3 | N/A | 0x0002 | 1 | 2 | 514 | 0x0514 | 1 | N/A | Fire state | Dampers closed (external/internal cause)
32 | 33 | 4x0033 | 3 | N/A | 0x0004 | 2 | 3 | 515 | 0x0515 | 1 | N/A | Smoke detector Loop error | Previous loop / temperature error
32 | 33 | 4x0033 | 3 | N/A | 0x0008 | 3 | 4 | 516 | 0x0516 | 1 | N/A | Damper 1 error
32 | 33 | 4x0033 | 3 | N/A | 0x0010 | 4 | 5 | 517 | 0x0517 | 1 | N/A | Function test state | Set while the local damper(s) exercise
32 | 33 | 4x0033 | 3 | N/A | 0x0020 | 5 | 6 | 518 | 0x0518 | 1 | N/A | Damper 2 error | Modules with two dampers, not SX:UNO
32 | 33 | 4x0033 | 3 | N/A | 0x0040 | 6 | 7 | 519 | 0x0519 | 1 | N/A | Dampers sum error
32 | 33 | 4x0033 | 3 | N/A | 0x0080 | 7 | 8 | 520 | 0x0520 | 1 | N/A | Over temperature (NTC) | Local alarm due to high temperature
32 | 33 | 4x0033 | 3 | N/A | 0x0100 | 8 | 9 | 521 | 0x0521 | 1 | N/A | Damper 1 closed
32 | 33 | 4x0033 | 3 | N/A | 0x0200 | 9 | 10 | 522 | 0x0522 | 1 | N/A | Damper 1 open
32 | 33 | 4x0033 | 3 | N/A | 0x0400 | 10 | 11 | 523 | 0x0523 | 1 | N/A | Damper 2 closed | Modules with two dampers, not SX:UNO
32 | 33 | 4x0033 | 3 | N/A | 0x0800 | 11 | 12 | 524 | 0x0524 | 1 | N/A | Damper 2 open | Modules with two dampers, not SX:UNO
32 | 33 | 4x0033 | 3 | N/A | 0x1000 | 12 | 13 | 525 | 0x0525 | 1 | N/A | Smoke detector normal run
32 | 33 | 4x0033 | 3 | N/A | 0x2000 | 13 | 14 | 526 | 0x0526 | 1 | N/A | Local alarm point state | Local fire (smoke detector) / temperature alarm
32 | 33 | 4x0033 | 3 | N/A | 0x4000 | 14 | 15 | 527 | 0x0527 | 1 | N/A | Smoke detector service alarm | Clean the detector
32 | 33 | 4x0033 | 3 | N/A | 0x8000 | 15 | 16 | 528 | 0x0528 | 1 | N/A | Smoke loop broken | Local smoke detector loop broken. Also sets local fire alarm (bit 526)
SX:UNO/DUO - Command Register
Address 0-base | Register 1-base | Modicon notation reg.read/write | Read reg func code | Write reg func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit nr. | Modicon notation bit read | Read bit func code | Write bit func code | Function | Action/remarks
44 | 45 | 4x0045 | 3 | 6 | 0x0001 | 0 | 1 | 705 | 0x0705 | 1 | 5 | Forced damper opening | Selective smoke exhaust, force damper opening during alarm
44 | 45 | 4x0045 | 3 | 6 | 0x0002 | 1 | 2 | 706 | 0x0706 | 1 | 5 | External fire alarm | External fire damper will close
44 | 45 | 4x0045 | 3 | 6 | 0x0004 | 2 | 3 | 707 | 0x0707 | 1 | 5 | Reset local alarms (smoke detector) | Automatically cleared
44 | 45 | 4x0045 | 3 | 6 | 0x0008 | 3 | 4 | 708 | 0x0708 | 1 | 5 | Close dampers | E.g. for night operation
44 | 45 | 4x0045 | 3 | 6 | 0x0010 | 4 | 5 | 709 | 0x0709 | 1 | 5 | Function test / Exercise | Automatically cleared
Note: Write only once when a command is issued and not continuously (Reset local alarms / Function test).
SX:UNO/DUO - Additional Registers
Address 0-base | Register 1-base | Modicon notation reg.read/write | Read reg func code | Write reg func code | Default value | Function |  |  | Action/remarks
32771 | 32772 | 4x32772 | 3 | 6 | 25 | Watchdog time/inputs debounce |  |  | Debounce 100ms and no watchdog at delivery. Calculation formula: Wtime(seconds) * 256 + 25 Note:max 255 seconds
32780 | 32781 | 4x32781 | 3 | 6 | 400 | Smoke detector loop level |  |  | Below=loop error=fire. 400=4mA
32781 | 32782 | 4x32782 | 3 | 6 | 1600 | Smoke detector service lev. |  |  | Above=Service request. 1600=16mA
32782 | 32783 | 4x32783 | 3 | 6 | 3000 | Smoke detector smoke lev. |  |  | Above=Fire. 3000=30mA
32783 | 32784 | 4x32784 | 3 | 6 | 0 | Over-temperature level |  |  | (unit 0,1ºC) 0=off, 720=72ºC
56 | 57 | 4x0057 | 3 | N/A | N/A | Temperature current value |  |  | (unit 0,1ºC). Read only RAM
57 | 58 | 4x0058 | 3 | N/A | N/A | Smoke detector current val |  |  | (unit μA * 10). Read only RAM
41 | 42 | 4x0042 | 3 | N/A | N/A | Time left to exercise |  |  | Hours left before exercise. Read only RAM
32803 | 32804 | 4x32804 | 3 | 6 | 48 | Exercise interval |  |  | Hours between exercise. 0=No automatic function test
32804 | 32805 | 4x32805 | 3 | 6 | 640 | Damper closing time |  |  | Max closing time (unit 1/16s). Default 40s
32810 | 32811 | 4x32811 | 3 | 6 | 2880 | Damper opening time |  |  | Max opening time (unit 1/16s). Default 180s
6 | 7 | 4x0007 | 3 | 6 | 4096 | Analog out, damper 1 |  |  | 0-4096=0-10V=0-100% open. Note:"Regulation alternative" must be set to 0 for remote control (default)
7 | 8 | 4x0008 | 3 | 6 | 4096 | Analog out, damper 2 |  |  | 0-4096=0-10V=0-100% open. Note:"Regulation alternative" must be set to 0 for remote control (default)
Note: Modbus registers 32xxx are stored in EEPROM (non-volatile memory). Do not write continuously to these, since each register is limited to maximum 1 million writes.