## SX_ACCESS functions
Product: |  |  |  |  | MODBUS TCP REGISTERS IN SX:ACCESS (8EX2:002)
SX:ACCESS (8EX2:002)
Important: Modbus TCP Slave Address for SX:ACCESS is 60. Always use port 502 for Modbus TCP communications to the module's IP-address.
Below is shown the register table in different notations.
To read the status registers for the damper modules directly from the SX:ACCESS (8EX2:002), please refer to Sheet 2.
EX2 Registers
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function
57 | 58 | 4x0058 | 3 | N/A | 0x0001 | 0 | 1 | 913 | 0x0913 | 1 | N/A | 1.21- | DI1. Bit set if input active (connection between terminals 1-2)
57 | 58 | 4x0058 | 3 | N/A | 0x0002 | 1 | 2 | 914 | 0x0914 | 1 | N/A | 1.21- | DI2. Bit set if input active (connection between terminals 3-4)
57 | 58 | 4x0058 | 3 | N/A | 0x0004 | 2 | 3 | 915 | 0x0915 | 1 | N/A | 1.21- | DI3. Bit set if input active (connection between terminals 5-6)
57 | 58 | 4x0058 | 3 | N/A | 0x0008 | 3 | 4 | 916 | 0x0916 | 1 | N/A | 1.21- | DI4. Bit set if input active (connection between terminals 7-8)
56 | 57 | 4x0056 | 3 | N/A | 0x0001 | 0 | 1 | 897 | 0x0897 | 1 | N/A | 1.21- | DO1. Bit set for sum alarm (communication error+damper failure). Relay opens
56 | 57 | 4x0056 | 3 | N/A | 0x0002 | 1 | 2 | 898 | 0x0898 | 1 | N/A | 1.21- | DO2. Bit set for fire alarm. Relay opens
56 | 57 | 4x0056 | 3 | N/A | 0x0004 | 2 | 3 | 899 | 0x0899 | 1 | N/A | 1.21- | DO3. Bit set for smoke detector service alarm. Relay opens
56 | 57 | 4x0056 | 3 | N/A | 0x0008 | 3 | 4 | 900 | 0x0900 | 1 | N/A | 1.21- | DO4. Run indication output. Bit cleared when selected condition(s) are satisfied and relay opens
56 | 57 | 4x0056 | 3 | N/A | 0x0010 | 4 | 5 | 901 | 0x0901 | 1 | N/A | 1.21- | OK LED. Bit set if LED active (normal no-alarm condition)
56 | 57 | 4x0056 | 3 | N/A | 0x0020 | 5 | 6 | 902 | 0x0902 | 1 | N/A | 1.21- | Alarm LED. Bit set if LED active
56 | 57 | 4x0056 | 3 | N/A | 0x0040 | 6 | 7 | 903 | 0x0903 | 1 | N/A | 1.21- | Error LED. Bit set if LED active
80 | 81 | 4x0081 | 3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.21- | Current value for number of fire alarms
81 | 82 | 4x0082 | 3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.21- | Current value for number of non-communicating modules
82 | 83 | 4x0083 | 3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.21- | Current value for number of damper failures
83 | 84 | 4x0084 | 3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.21- | Current value for number of service alarms for smoke detectors
84 | 85 | 4x0085 | 3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.21- | Current value for number of exercising modules
124 | 125 | 4x0125 | 3 | N/A | 0x0001 | 0 | 1 | 1985 | 0x1985 | 1 | N/A | 1.49- | If in "Service mode" then register read=1, bit read=1
125 | 126 | 4x0126 | N/A | 6 | 0x0001 | 0 | 1 | 2001 | 0x2001 | N/A | 5 | 1.49- | Writing 1 (as register or bit) then module exits from "Service mode"
160 | 161 | 4x0161 | 3 | 6 | 0x0001 | 0 | 1 | 2561 | 0x2561 | 1 | 5 | 1.21- | Bit activates night mode, all dampers will close
161 | 162 | 4x0162 | 3 | 6 | 0x0001 | 0 | 1 | 2577 | 0x2577 | 1 | 5 | 1.21- | Bit activates exercise for all dampers. No exercise is performed if the module is in “Service mode”. If so, the dampers will be kept open. Bit is automatically cleared.
197 | 198 | 4x0198 | 3 | 6 | 0x0001 | 0 | 1 | 3153 | 0x3153 | 1 | 5 | 2.03- | A change of the bit from 0 to 1 requests "reset all smoke detectors". User has to clear the bit by writing 0 in preparation for a future reset request by then writing 1 again.
197 | 198 | 4x0198 | 3 | 6 | 0x0002 | 1 | 2 | 3154 | 0x3154 | 1 | 5 | 2.03- | This bit is set when the "reset all smoke detectors" operation is complete and can be used to detect that the operation is finished. If the bit is used, the user must clear the bit before the next "reset all smoke detectors" operation is requested.
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
40 | 41 | 4x0041 | 3 | 6 | 0x0001 | 0 | 1 | 641 | 0x0641 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 1
40 | 41 | 4x0041 | 3 | 6 | 0x0002 | 1 | 2 | 642 | 0x0642 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 2
40 | 41 | 4x0041 | 3 | 6 | 0x0004 | 2 | 3 | 643 | 0x0643 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 3
40 | 41 | 4x0041 | 3 | 6 | 0x0008 | 3 | 4 | 644 | 0x0644 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 4
40 | 41 | 4x0041 | 3 | 6 | 0x0010 | 4 | 5 | 645 | 0x0645 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 5
40 | 41 | 4x0041 | 3 | 6 | 0x0020 | 5 | 6 | 646 | 0x0646 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 6
40 | 41 | 4x0041 | 3 | 6 | 0x0040 | 6 | 7 | 647 | 0x0647 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 7
40 | 41 | 4x0041 | 3 | 6 | 0x0080 | 7 | 8 | 648 | 0x0648 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 8
40 | 41 | 4x0041 | 3 | 6 | 0x0100 | 8 | 9 | 649 | 0x0649 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 9
40 | 41 | 4x0041 | 3 | 6 | 0x0200 | 9 | 10 | 650 | 0x0650 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 10
40 | 41 | 4x0041 | 3 | 6 | 0x0400 | 10 | 11 | 651 | 0x0651 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 11
40 | 41 | 4x0041 | 3 | 6 | 0x0800 | 11 | 12 | 652 | 0x0652 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 12
40 | 41 | 4x0041 | 3 | 6 | 0x1000 | 12 | 13 | 653 | 0x0653 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 13
40 | 41 | 4x0041 | 3 | 6 | 0x2000 | 13 | 14 | 654 | 0x0654 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 14
40 | 41 | 4x0041 | 3 | 6 | 0x4000 | 14 | 15 | 655 | 0x0655 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 15
40 | 41 | 4x0041 | 3 | 6 | 0x8000 | 15 | 16 | 656 | 0x0656 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 16
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
41 | 42 | 4x0042 | 3 | 6 | 0x0001 | 0 | 1 | 657 | 0x0657 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 17
41 | 42 | 4x0042 | 3 | 6 | 0x0002 | 1 | 2 | 658 | 0x0658 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 18
41 | 42 | 4x0042 | 3 | 6 | 0x0004 | 2 | 3 | 659 | 0x0659 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 19
41 | 42 | 4x0042 | 3 | 6 | 0x0008 | 3 | 4 | 660 | 0x0660 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 20
41 | 42 | 4x0042 | 3 | 6 | 0x0010 | 4 | 5 | 661 | 0x0661 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 21
41 | 42 | 4x0042 | 3 | 6 | 0x0020 | 5 | 6 | 662 | 0x0662 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 22
41 | 42 | 4x0042 | 3 | 6 | 0x0040 | 6 | 7 | 663 | 0x0663 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 23
41 | 42 | 4x0042 | 3 | 6 | 0x0080 | 7 | 8 | 664 | 0x0664 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 24
41 | 42 | 4x0042 | 3 | 6 | 0x0100 | 8 | 9 | 665 | 0x0665 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 25
41 | 42 | 4x0042 | 3 | 6 | 0x0200 | 9 | 10 | 666 | 0x0666 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 26
41 | 42 | 4x0042 | 3 | 6 | 0x0400 | 10 | 11 | 667 | 0x0667 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 27
41 | 42 | 4x0042 | 3 | 6 | 0x0800 | 11 | 12 | 668 | 0x0668 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 28
41 | 42 | 4x0042 | 3 | 6 | 0x1000 | 12 | 13 | 669 | 0x0669 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 29
41 | 42 | 4x0042 | 3 | 6 | 0x2000 | 13 | 14 | 670 | 0x0670 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 30
41 | 42 | 4x0042 | 3 | 6 | 0x4000 | 14 | 15 | 671 | 0x0671 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 31
41 | 42 | 4x0042 | 3 | 6 | 0x8000 | 15 | 16 | 672 | 0x0672 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 32
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
42 | 43 | 4x0043 | 3 | 6 | 0x0001 | 0 | 1 | 673 | 0x0673 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 33
42 | 43 | 4x0043 | 3 | 6 | 0x0002 | 1 | 2 | 674 | 0x0674 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 34
42 | 43 | 4x0043 | 3 | 6 | 0x0004 | 2 | 3 | 675 | 0x0675 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 35
42 | 43 | 4x0043 | 3 | 6 | 0x0008 | 3 | 4 | 676 | 0x0676 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 36
42 | 43 | 4x0043 | 3 | 6 | 0x0010 | 4 | 5 | 677 | 0x0677 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 37
42 | 43 | 4x0043 | 3 | 6 | 0x0020 | 5 | 6 | 678 | 0x0678 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 38
42 | 43 | 4x0043 | 3 | 6 | 0x0040 | 6 | 7 | 679 | 0x0679 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 39
42 | 43 | 4x0043 | 3 | 6 | 0x0080 | 7 | 8 | 680 | 0x0680 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 40
42 | 43 | 4x0043 | 3 | 6 | 0x0100 | 8 | 9 | 681 | 0x0681 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 41
42 | 43 | 4x0043 | 3 | 6 | 0x0200 | 9 | 10 | 682 | 0x0682 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 42
42 | 43 | 4x0043 | 3 | 6 | 0x0400 | 10 | 11 | 683 | 0x0683 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 43
42 | 43 | 4x0043 | 3 | 6 | 0x0800 | 11 | 12 | 684 | 0x0684 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 44
42 | 43 | 4x0043 | 3 | 6 | 0x1000 | 12 | 13 | 685 | 0x0685 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 45
42 | 43 | 4x0043 | 3 | 6 | 0x2000 | 13 | 14 | 686 | 0x0686 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 46
42 | 43 | 4x0043 | 3 | 6 | 0x4000 | 14 | 15 | 687 | 0x0687 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 47
42 | 43 | 4x0043 | 3 | 6 | 0x8000 | 15 | 16 | 688 | 0x0688 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 48
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
43 | 44 | 4x0044 | 3 | 6 | 0x0001 | 0 | 1 | 689 | 0x0689 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 49
43 | 44 | 4x0044 | 3 | 6 | 0x0002 | 1 | 2 | 690 | 0x0690 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 50
43 | 44 | 4x0044 | 3 | 6 | 0x0004 | 2 | 3 | 691 | 0x0691 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 51
43 | 44 | 4x0044 | 3 | 6 | 0x0008 | 3 | 4 | 692 | 0x0692 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 52
43 | 44 | 4x0044 | 3 | 6 | 0x0010 | 4 | 5 | 693 | 0x0693 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 53
43 | 44 | 4x0044 | 3 | 6 | 0x0020 | 5 | 6 | 694 | 0x0694 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 54
43 | 44 | 4x0044 | 3 | 6 | 0x0040 | 6 | 7 | 695 | 0x0695 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 55
43 | 44 | 4x0044 | 3 | 6 | 0x0080 | 7 | 8 | 696 | 0x0696 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 56
43 | 44 | 4x0044 | 3 | 6 | 0x0100 | 8 | 9 | 697 | 0x0697 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 57
43 | 44 | 4x0044 | 3 | 6 | 0x0200 | 9 | 10 | 698 | 0x0698 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 58
43 | 44 | 4x0044 | 3 | 6 | 0x0400 | 10 | 11 | 699 | 0x0699 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 59
43 | 44 | 4x0044 | 3 | 6 | 0x0800 | 11 | 12 | 700 | 0x0700 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 60
43 | 44 | 4x0044 | 3 | 6 | 0x1000 | 12 | 13 | 701 | 0x0701 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 61
43 | 44 | 4x0044 | 3 | 6 | 0x2000 | 13 | 14 | 702 | 0x0702 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 62
43 | 44 | 4x0044 | 3 | 6 | 0x4000 | 14 | 15 | 703 | 0x0703 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 63
43 | 44 | 4x0044 | 3 | 6 | 0x8000 | 15 | 16 | 704 | 0x0704 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 64
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
44 | 45 | 4x0045 | 3 | 6 | 0x0001 | 0 | 1 | 705 | 0x0705 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 65
44 | 45 | 4x0045 | 3 | 6 | 0x0002 | 1 | 2 | 706 | 0x0706 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 66
44 | 45 | 4x0045 | 3 | 6 | 0x0004 | 2 | 3 | 707 | 0x0707 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 67
44 | 45 | 4x0045 | 3 | 6 | 0x0008 | 3 | 4 | 708 | 0x0708 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 68
44 | 45 | 4x0045 | 3 | 6 | 0x0010 | 4 | 5 | 709 | 0x0709 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 69
44 | 45 | 4x0045 | 3 | 6 | 0x0020 | 5 | 6 | 710 | 0x0710 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 70
44 | 45 | 4x0045 | 3 | 6 | 0x0040 | 6 | 7 | 711 | 0x0711 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 71
44 | 45 | 4x0045 | 3 | 6 | 0x0080 | 7 | 8 | 712 | 0x0712 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 72
44 | 45 | 4x0045 | 3 | 6 | 0x0100 | 8 | 9 | 713 | 0x0713 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 73
44 | 45 | 4x0045 | 3 | 6 | 0x0200 | 9 | 10 | 714 | 0x0714 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 74
44 | 45 | 4x0045 | 3 | 6 | 0x0400 | 10 | 11 | 715 | 0x0715 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 75
44 | 45 | 4x0045 | 3 | 6 | 0x0800 | 11 | 12 | 716 | 0x0716 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 76
44 | 45 | 4x0045 | 3 | 6 | 0x1000 | 12 | 13 | 717 | 0x0717 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 77
44 | 45 | 4x0045 | 3 | 6 | 0x2000 | 13 | 14 | 718 | 0x0718 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 78
44 | 45 | 4x0045 | 3 | 6 | 0x4000 | 14 | 15 | 719 | 0x0719 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 79
44 | 45 | 4x0045 | 3 | 6 | 0x8000 | 15 | 16 | 720 | 0x0720 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 80
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
45 | 46 | 4x0046 | 3 | 6 | 0x0001 | 0 | 1 | 721 | 0x0721 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 81
45 | 46 | 4x0046 | 3 | 6 | 0x0002 | 1 | 2 | 722 | 0x0722 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 82
45 | 46 | 4x0046 | 3 | 6 | 0x0004 | 2 | 3 | 723 | 0x0723 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 83
45 | 46 | 4x0046 | 3 | 6 | 0x0008 | 3 | 4 | 724 | 0x0724 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 84
45 | 46 | 4x0046 | 3 | 6 | 0x0010 | 4 | 5 | 725 | 0x0725 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 85
45 | 46 | 4x0046 | 3 | 6 | 0x0020 | 5 | 6 | 726 | 0x0726 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 86
45 | 46 | 4x0046 | 3 | 6 | 0x0040 | 6 | 7 | 727 | 0x0727 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 87
45 | 46 | 4x0046 | 3 | 6 | 0x0080 | 7 | 8 | 728 | 0x0728 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 88
45 | 46 | 4x0046 | 3 | 6 | 0x0100 | 8 | 9 | 729 | 0x0729 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 89
45 | 46 | 4x0046 | 3 | 6 | 0x0200 | 9 | 10 | 730 | 0x0730 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 90
45 | 46 | 4x0046 | 3 | 6 | 0x0400 | 10 | 11 | 731 | 0x0731 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 91
45 | 46 | 4x0046 | 3 | 6 | 0x0800 | 11 | 12 | 732 | 0x0732 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 92
45 | 46 | 4x0046 | 3 | 6 | 0x1000 | 12 | 13 | 733 | 0x0733 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 93
45 | 46 | 4x0046 | 3 | 6 | 0x2000 | 13 | 14 | 734 | 0x0734 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 94
45 | 46 | 4x0046 | 3 | 6 | 0x4000 | 14 | 15 | 735 | 0x0735 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 95
45 | 46 | 4x0046 | 3 | 6 | 0x8000 | 15 | 16 | 736 | 0x0736 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 96
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
46 | 47 | 4x0047 | 3 | 6 | 0x0001 | 0 | 1 | 737 | 0x0737 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 97
46 | 47 | 4x0047 | 3 | 6 | 0x0002 | 1 | 2 | 738 | 0x0738 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 98
46 | 47 | 4x0047 | 3 | 6 | 0x0004 | 2 | 3 | 739 | 0x0739 | 1 | 5 | 1.60- | Close all dampers in fire cell (night mode). Set bit=close dampers | 99
Below registers 162-168 should only be used for testing purposes. Because no watch of the
Modbus communication is available they should not be used for real fire alarms UNLESS the
Modbus communication watchdog is used.
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
162 | 163 | 4x0163 | 3 | 6 | 0x0001 | 0 | 1 | 2593 | 0x2593 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 1
162 | 163 | 4x0163 | 3 | 6 | 0x0002 | 1 | 2 | 2594 | 0x2594 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 2
162 | 163 | 4x0163 | 3 | 6 | 0x0004 | 2 | 3 | 2595 | 0x2595 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 3
162 | 163 | 4x0163 | 3 | 6 | 0x0008 | 3 | 4 | 2596 | 0x2596 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 4
162 | 163 | 4x0163 | 3 | 6 | 0x0010 | 4 | 5 | 2597 | 0x2597 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 5
162 | 163 | 4x0163 | 3 | 6 | 0x0020 | 5 | 6 | 2598 | 0x2598 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 6
162 | 163 | 4x0163 | 3 | 6 | 0x0040 | 6 | 7 | 2599 | 0x2599 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 7
162 | 163 | 4x0163 | 3 | 6 | 0x0080 | 7 | 8 | 2600 | 0x2600 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 8
162 | 163 | 4x0163 | 3 | 6 | 0x0100 | 8 | 9 | 2601 | 0x2601 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 9
162 | 163 | 4x0163 | 3 | 6 | 0x0200 | 9 | 10 | 2602 | 0x2602 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 10
162 | 163 | 4x0163 | 3 | 6 | 0x0400 | 10 | 11 | 2603 | 0x2603 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 11
162 | 163 | 4x0163 | 3 | 6 | 0x0800 | 11 | 12 | 2604 | 0x2604 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 12
162 | 163 | 4x0163 | 3 | 6 | 0x1000 | 12 | 13 | 2605 | 0x2605 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 13
162 | 163 | 4x0163 | 3 | 6 | 0x2000 | 13 | 14 | 2606 | 0x2606 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 14
162 | 163 | 4x0163 | 3 | 6 | 0x4000 | 14 | 15 | 2607 | 0x2607 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 15
162 | 163 | 4x0163 | 3 | 6 | 0x8000 | 15 | 16 | 2608 | 0x2608 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 16
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
163 | 164 | 4x0164 | 3 | 6 | 0x0001 | 0 | 1 | 2609 | 0x2609 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 17
163 | 164 | 4x0164 | 3 | 6 | 0x0002 | 1 | 2 | 2610 | 0x2610 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 18
163 | 164 | 4x0164 | 3 | 6 | 0x0004 | 2 | 3 | 2611 | 0x2611 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 19
163 | 164 | 4x0164 | 3 | 6 | 0x0008 | 3 | 4 | 2612 | 0x2612 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 20
163 | 164 | 4x0164 | 3 | 6 | 0x0010 | 4 | 5 | 2613 | 0x2613 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 21
163 | 164 | 4x0164 | 3 | 6 | 0x0020 | 5 | 6 | 2614 | 0x2614 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 22
163 | 164 | 4x0164 | 3 | 6 | 0x0040 | 6 | 7 | 2615 | 0x2615 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 23
163 | 164 | 4x0164 | 3 | 6 | 0x0080 | 7 | 8 | 2616 | 0x2616 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 24
163 | 164 | 4x0164 | 3 | 6 | 0x0100 | 8 | 9 | 2617 | 0x2617 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 25
163 | 164 | 4x0164 | 3 | 6 | 0x0200 | 9 | 10 | 2618 | 0x2618 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 26
163 | 164 | 4x0164 | 3 | 6 | 0x0400 | 10 | 11 | 2619 | 0x2619 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 27
163 | 164 | 4x0164 | 3 | 6 | 0x0800 | 11 | 12 | 2620 | 0x2620 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 28
163 | 164 | 4x0164 | 3 | 6 | 0x1000 | 12 | 13 | 2621 | 0x2621 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 29
163 | 164 | 4x0164 | 3 | 6 | 0x2000 | 13 | 14 | 2622 | 0x2622 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 30
163 | 164 | 4x0164 | 3 | 6 | 0x4000 | 14 | 15 | 2623 | 0x2623 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 31
163 | 164 | 4x0164 | 3 | 6 | 0x8000 | 15 | 16 | 2624 | 0x2624 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 32
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
164 | 165 | 4x0165 | 3 | 6 | 0x0001 | 0 | 1 | 2625 | 0x2625 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 33
164 | 165 | 4x0165 | 3 | 6 | 0x0002 | 1 | 2 | 2626 | 0x2626 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 34
164 | 165 | 4x0165 | 3 | 6 | 0x0004 | 2 | 3 | 2627 | 0x2627 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 35
164 | 165 | 4x0165 | 3 | 6 | 0x0008 | 3 | 4 | 2628 | 0x2628 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 36
164 | 165 | 4x0165 | 3 | 6 | 0x0010 | 4 | 5 | 2629 | 0x2629 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 37
164 | 165 | 4x0165 | 3 | 6 | 0x0020 | 5 | 6 | 2630 | 0x2630 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 38
164 | 165 | 4x0165 | 3 | 6 | 0x0040 | 6 | 7 | 2631 | 0x2631 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 39
164 | 165 | 4x0165 | 3 | 6 | 0x0080 | 7 | 8 | 2632 | 0x2632 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 40
164 | 165 | 4x0165 | 3 | 6 | 0x0100 | 8 | 9 | 2633 | 0x2633 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 41
164 | 165 | 4x0165 | 3 | 6 | 0x0200 | 9 | 10 | 2634 | 0x2634 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 42
164 | 165 | 4x0165 | 3 | 6 | 0x0400 | 10 | 11 | 2635 | 0x2635 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 43
164 | 165 | 4x0165 | 3 | 6 | 0x0800 | 11 | 12 | 2636 | 0x2636 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 44
164 | 165 | 4x0165 | 3 | 6 | 0x1000 | 12 | 13 | 2637 | 0x2637 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 45
164 | 165 | 4x0165 | 3 | 6 | 0x2000 | 13 | 14 | 2638 | 0x2638 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 46
164 | 165 | 4x0165 | 3 | 6 | 0x4000 | 14 | 15 | 2639 | 0x2639 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 47
164 | 165 | 4x0165 | 3 | 6 | 0x8000 | 15 | 16 | 2640 | 0x2640 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 48
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
165 | 166 | 4x0166 | 3 | 6 | 0x0001 | 0 | 1 | 2641 | 0x2641 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 49
165 | 166 | 4x0166 | 3 | 6 | 0x0002 | 1 | 2 | 2642 | 0x2642 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 50
165 | 166 | 4x0166 | 3 | 6 | 0x0004 | 2 | 3 | 2643 | 0x2643 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 51
165 | 166 | 4x0166 | 3 | 6 | 0x0008 | 3 | 4 | 2644 | 0x2644 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 52
165 | 166 | 4x0166 | 3 | 6 | 0x0010 | 4 | 5 | 2645 | 0x2645 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 53
165 | 166 | 4x0166 | 3 | 6 | 0x0020 | 5 | 6 | 2646 | 0x2646 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 54
165 | 166 | 4x0166 | 3 | 6 | 0x0040 | 6 | 7 | 2647 | 0x2647 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 55
165 | 166 | 4x0166 | 3 | 6 | 0x0080 | 7 | 8 | 2648 | 0x2648 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 56
165 | 166 | 4x0166 | 3 | 6 | 0x0100 | 8 | 9 | 2649 | 0x2649 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 57
165 | 166 | 4x0166 | 3 | 6 | 0x0200 | 9 | 10 | 2650 | 0x2650 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 58
165 | 166 | 4x0166 | 3 | 6 | 0x0400 | 10 | 11 | 2651 | 0x2651 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 59
165 | 166 | 4x0166 | 3 | 6 | 0x0800 | 11 | 12 | 2652 | 0x2652 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 60
165 | 166 | 4x0166 | 3 | 6 | 0x1000 | 12 | 13 | 2653 | 0x2653 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 61
165 | 166 | 4x0166 | 3 | 6 | 0x2000 | 13 | 14 | 2654 | 0x2654 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 62
165 | 166 | 4x0166 | 3 | 6 | 0x4000 | 14 | 15 | 2655 | 0x2655 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 63
165 | 166 | 4x0166 | 3 | 6 | 0x8000 | 15 | 16 | 2656 | 0x2656 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 64
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
166 | 167 | 4x0167 | 3 | 6 | 0x0001 | 0 | 1 | 2657 | 0x2657 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 65
166 | 167 | 4x0167 | 3 | 6 | 0x0002 | 1 | 2 | 2658 | 0x2658 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 66
166 | 167 | 4x0167 | 3 | 6 | 0x0004 | 2 | 3 | 2659 | 0x2659 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 67
166 | 167 | 4x0167 | 3 | 6 | 0x0008 | 3 | 4 | 2660 | 0x2660 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 68
166 | 167 | 4x0167 | 3 | 6 | 0x0010 | 4 | 5 | 2661 | 0x2661 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 69
166 | 167 | 4x0167 | 3 | 6 | 0x0020 | 5 | 6 | 2662 | 0x2662 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 70
166 | 167 | 4x0167 | 3 | 6 | 0x0040 | 6 | 7 | 2663 | 0x2663 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 71
166 | 167 | 4x0167 | 3 | 6 | 0x0080 | 7 | 8 | 2664 | 0x2664 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 72
166 | 167 | 4x0167 | 3 | 6 | 0x0100 | 8 | 9 | 2665 | 0x2665 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 73
166 | 167 | 4x0167 | 3 | 6 | 0x0200 | 9 | 10 | 2666 | 0x2666 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 74
166 | 167 | 4x0167 | 3 | 6 | 0x0400 | 10 | 11 | 2667 | 0x2667 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 75
166 | 167 | 4x0167 | 3 | 6 | 0x0800 | 11 | 12 | 2668 | 0x2668 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 76
166 | 167 | 4x0167 | 3 | 6 | 0x1000 | 12 | 13 | 2669 | 0x2669 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 77
166 | 167 | 4x0167 | 3 | 6 | 0x2000 | 13 | 14 | 2670 | 0x2670 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 78
166 | 167 | 4x0167 | 3 | 6 | 0x4000 | 14 | 15 | 2671 | 0x2671 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 79
166 | 167 | 4x0167 | 3 | 6 | 0x8000 | 15 | 16 | 2672 | 0x2672 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 80
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
167 | 168 | 4x0168 | 3 | 6 | 0x0001 | 0 | 1 | 2673 | 0x2673 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 81
167 | 168 | 4x0168 | 3 | 6 | 0x0002 | 1 | 2 | 2674 | 0x2674 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 82
167 | 168 | 4x0168 | 3 | 6 | 0x0004 | 2 | 3 | 2675 | 0x2675 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 83
167 | 168 | 4x0168 | 3 | 6 | 0x0008 | 3 | 4 | 2676 | 0x2676 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 84
167 | 168 | 4x0168 | 3 | 6 | 0x0010 | 4 | 5 | 2677 | 0x2677 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 85
167 | 168 | 4x0168 | 3 | 6 | 0x0020 | 5 | 6 | 2678 | 0x2678 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 86
167 | 168 | 4x0168 | 3 | 6 | 0x0040 | 6 | 7 | 2679 | 0x2679 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 87
167 | 168 | 4x0168 | 3 | 6 | 0x0080 | 7 | 8 | 2680 | 0x2680 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 88
167 | 168 | 4x0168 | 3 | 6 | 0x0100 | 8 | 9 | 2681 | 0x2681 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 89
167 | 168 | 4x0168 | 3 | 6 | 0x0200 | 9 | 10 | 2682 | 0x2682 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 90
167 | 168 | 4x0168 | 3 | 6 | 0x0400 | 10 | 11 | 2683 | 0x2683 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 91
167 | 168 | 4x0168 | 3 | 6 | 0x0800 | 11 | 12 | 2684 | 0x2684 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 92
167 | 168 | 4x0168 | 3 | 6 | 0x1000 | 12 | 13 | 2685 | 0x2685 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 93
167 | 168 | 4x0168 | 3 | 6 | 0x2000 | 13 | 14 | 2686 | 0x2686 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 94
167 | 168 | 4x0168 | 3 | 6 | 0x4000 | 14 | 15 | 2687 | 0x2687 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 95
167 | 168 | 4x0168 | 3 | 6 | 0x8000 | 15 | 16 | 2688 | 0x2688 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 96
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
168 | 169 | 4x0169 | 3 | 6 | 0x0001 | 0 | 1 | 2689 | 0x2689 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 97
168 | 169 | 4x0169 | 3 | 6 | 0x0002 | 1 | 2 | 2690 | 0x2690 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 98
168 | 169 | 4x0169 | 3 | 6 | 0x0004 | 2 | 3 | 2691 | 0x2691 | 1 | 5 | 1.21- | Bit sets fire in fire cell. Set bit=fire | 99
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
169 | 170 | 4x0170 | 3 | N/A | 0x0001 | 0 | 1 | 2705 | 0x2705 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 1
169 | 170 | 4x0170 | 3 | N/A | 0x0002 | 1 | 2 | 2706 | 0x2706 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 2
169 | 170 | 4x0170 | 3 | N/A | 0x0004 | 2 | 3 | 2707 | 0x2707 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 3
169 | 170 | 4x0170 | 3 | N/A | 0x0008 | 3 | 4 | 2708 | 0x2708 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 4
169 | 170 | 4x0170 | 3 | N/A | 0x0010 | 4 | 5 | 2709 | 0x2709 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 5
169 | 170 | 4x0170 | 3 | N/A | 0x0020 | 5 | 6 | 2710 | 0x2710 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 6
169 | 170 | 4x0170 | 3 | N/A | 0x0040 | 6 | 7 | 2711 | 0x2711 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 7
169 | 170 | 4x0170 | 3 | N/A | 0x0080 | 7 | 8 | 2712 | 0x2712 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 8
169 | 170 | 4x0170 | 3 | N/A | 0x0100 | 8 | 9 | 2713 | 0x2713 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 9
169 | 170 | 4x0170 | 3 | N/A | 0x0200 | 9 | 10 | 2714 | 0x2714 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 10
169 | 170 | 4x0170 | 3 | N/A | 0x0400 | 10 | 11 | 2715 | 0x2715 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 11
169 | 170 | 4x0170 | 3 | N/A | 0x0800 | 11 | 12 | 2716 | 0x2716 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 12
169 | 170 | 4x0170 | 3 | N/A | 0x1000 | 12 | 13 | 2717 | 0x2717 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 13
169 | 170 | 4x0170 | 3 | N/A | 0x2000 | 13 | 14 | 2718 | 0x2718 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 14
169 | 170 | 4x0170 | 3 | N/A | 0x4000 | 14 | 15 | 2719 | 0x2719 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 15
169 | 170 | 4x0170 | 3 | N/A | 0x8000 | 15 | 16 | 2720 | 0x2720 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 16
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
170 | 171 | 4x0171 | 3 | N/A | 0x0001 | 0 | 1 | 2721 | 0x2721 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 17
170 | 171 | 4x0171 | 3 | N/A | 0x0002 | 1 | 2 | 2722 | 0x2722 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 18
170 | 171 | 4x0171 | 3 | N/A | 0x0004 | 2 | 3 | 2723 | 0x2723 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 19
170 | 171 | 4x0171 | 3 | N/A | 0x0008 | 3 | 4 | 2724 | 0x2724 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 20
170 | 171 | 4x0171 | 3 | N/A | 0x0010 | 4 | 5 | 2725 | 0x2725 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 21
170 | 171 | 4x0171 | 3 | N/A | 0x0020 | 5 | 6 | 2726 | 0x2726 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 22
170 | 171 | 4x0171 | 3 | N/A | 0x0040 | 6 | 7 | 2727 | 0x2727 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 23
170 | 171 | 4x0171 | 3 | N/A | 0x0080 | 7 | 8 | 2728 | 0x2728 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 24
170 | 171 | 4x0171 | 3 | N/A | 0x0100 | 8 | 9 | 2729 | 0x2729 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 25
170 | 171 | 4x0171 | 3 | N/A | 0x0200 | 9 | 10 | 2730 | 0x2730 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 26
170 | 171 | 4x0171 | 3 | N/A | 0x0400 | 10 | 11 | 2731 | 0x2731 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 27
170 | 171 | 4x0171 | 3 | N/A | 0x0800 | 11 | 12 | 2732 | 0x2732 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 28
170 | 171 | 4x0171 | 3 | N/A | 0x1000 | 12 | 13 | 2733 | 0x2733 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 29
170 | 171 | 4x0171 | 3 | N/A | 0x2000 | 13 | 14 | 2734 | 0x2734 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 30
170 | 171 | 4x0171 | 3 | N/A | 0x4000 | 14 | 15 | 2735 | 0x2735 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 31
170 | 171 | 4x0171 | 3 | N/A | 0x8000 | 15 | 16 | 2736 | 0x2736 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 32
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
171 | 172 | 4x0172 | 3 | N/A | 0x0001 | 0 | 1 | 2737 | 0x2737 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 33
171 | 172 | 4x0172 | 3 | N/A | 0x0002 | 1 | 2 | 2738 | 0x2738 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 34
171 | 172 | 4x0172 | 3 | N/A | 0x0004 | 2 | 3 | 2739 | 0x2739 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 35
171 | 172 | 4x0172 | 3 | N/A | 0x0008 | 3 | 4 | 2740 | 0x2740 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 36
171 | 172 | 4x0172 | 3 | N/A | 0x0010 | 4 | 5 | 2741 | 0x2741 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 37
171 | 172 | 4x0172 | 3 | N/A | 0x0020 | 5 | 6 | 2742 | 0x2742 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 38
171 | 172 | 4x0172 | 3 | N/A | 0x0040 | 6 | 7 | 2743 | 0x2743 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 39
171 | 172 | 4x0172 | 3 | N/A | 0x0080 | 7 | 8 | 2744 | 0x2744 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 40
171 | 172 | 4x0172 | 3 | N/A | 0x0100 | 8 | 9 | 2745 | 0x2745 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 41
171 | 172 | 4x0172 | 3 | N/A | 0x0200 | 9 | 10 | 2746 | 0x2746 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 42
171 | 172 | 4x0172 | 3 | N/A | 0x0400 | 10 | 11 | 2747 | 0x2747 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 43
171 | 172 | 4x0172 | 3 | N/A | 0x0800 | 11 | 12 | 2748 | 0x2748 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 44
171 | 172 | 4x0172 | 3 | N/A | 0x1000 | 12 | 13 | 2749 | 0x2749 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 45
171 | 172 | 4x0172 | 3 | N/A | 0x2000 | 13 | 14 | 2750 | 0x2750 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 46
171 | 172 | 4x0172 | 3 | N/A | 0x4000 | 14 | 15 | 2751 | 0x2751 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 47
171 | 172 | 4x0172 | 3 | N/A | 0x8000 | 15 | 16 | 2752 | 0x2752 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 48
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
172 | 173 | 4x0173 | 3 | N/A | 0x0001 | 0 | 1 | 2753 | 0x2753 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 49
172 | 173 | 4x0173 | 3 | N/A | 0x0002 | 1 | 2 | 2754 | 0x2754 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 50
172 | 173 | 4x0173 | 3 | N/A | 0x0004 | 2 | 3 | 2755 | 0x2755 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 51
172 | 173 | 4x0173 | 3 | N/A | 0x0008 | 3 | 4 | 2756 | 0x2756 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 52
172 | 173 | 4x0173 | 3 | N/A | 0x0010 | 4 | 5 | 2757 | 0x2757 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 53
172 | 173 | 4x0173 | 3 | N/A | 0x0020 | 5 | 6 | 2758 | 0x2758 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 54
172 | 173 | 4x0173 | 3 | N/A | 0x0040 | 6 | 7 | 2759 | 0x2759 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 55
172 | 173 | 4x0173 | 3 | N/A | 0x0080 | 7 | 8 | 2760 | 0x2760 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 56
172 | 173 | 4x0173 | 3 | N/A | 0x0100 | 8 | 9 | 2761 | 0x2761 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 57
172 | 173 | 4x0173 | 3 | N/A | 0x0200 | 9 | 10 | 2762 | 0x2762 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 58
172 | 173 | 4x0173 | 3 | N/A | 0x0400 | 10 | 11 | 2763 | 0x2763 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 59
172 | 173 | 4x0173 | 3 | N/A | 0x0800 | 11 | 12 | 2764 | 0x2764 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 60
172 | 173 | 4x0173 | 3 | N/A | 0x1000 | 12 | 13 | 2765 | 0x2765 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 61
172 | 173 | 4x0173 | 3 | N/A | 0x2000 | 13 | 14 | 2766 | 0x2766 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 62
172 | 173 | 4x0173 | 3 | N/A | 0x4000 | 14 | 15 | 2767 | 0x2767 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 63
172 | 173 | 4x0173 | 3 | N/A | 0x8000 | 15 | 16 | 2768 | 0x2768 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 64
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
173 | 174 | 4x0174 | 3 | N/A | 0x0001 | 0 | 1 | 2769 | 0x2769 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 65
173 | 174 | 4x0174 | 3 | N/A | 0x0002 | 1 | 2 | 2770 | 0x2770 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 66
173 | 174 | 4x0174 | 3 | N/A | 0x0004 | 2 | 3 | 2771 | 0x2771 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 67
173 | 174 | 4x0174 | 3 | N/A | 0x0008 | 3 | 4 | 2772 | 0x2772 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 68
173 | 174 | 4x0174 | 3 | N/A | 0x0010 | 4 | 5 | 2773 | 0x2773 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 69
173 | 174 | 4x0174 | 3 | N/A | 0x0020 | 5 | 6 | 2774 | 0x2774 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 70
173 | 174 | 4x0174 | 3 | N/A | 0x0040 | 6 | 7 | 2775 | 0x2775 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 71
173 | 174 | 4x0174 | 3 | N/A | 0x0080 | 7 | 8 | 2776 | 0x2776 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 72
173 | 174 | 4x0174 | 3 | N/A | 0x0100 | 8 | 9 | 2777 | 0x2777 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 73
173 | 174 | 4x0174 | 3 | N/A | 0x0200 | 9 | 10 | 2778 | 0x2778 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 74
173 | 174 | 4x0174 | 3 | N/A | 0x0400 | 10 | 11 | 2779 | 0x2779 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 75
173 | 174 | 4x0174 | 3 | N/A | 0x0800 | 11 | 12 | 2780 | 0x2780 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 76
173 | 174 | 4x0174 | 3 | N/A | 0x1000 | 12 | 13 | 2781 | 0x2781 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 77
173 | 174 | 4x0174 | 3 | N/A | 0x2000 | 13 | 14 | 2782 | 0x2782 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 78
173 | 174 | 4x0174 | 3 | N/A | 0x4000 | 14 | 15 | 2783 | 0x2783 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 79
173 | 174 | 4x0174 | 3 | N/A | 0x8000 | 15 | 16 | 2784 | 0x2784 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 80
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
174 | 175 | 4x0175 | 3 | N/A | 0x0001 | 0 | 1 | 2785 | 0x2785 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 81
174 | 175 | 4x0175 | 3 | N/A | 0x0002 | 1 | 2 | 2786 | 0x2786 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 82
174 | 175 | 4x0175 | 3 | N/A | 0x0004 | 2 | 3 | 2787 | 0x2787 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 83
174 | 175 | 4x0175 | 3 | N/A | 0x0008 | 3 | 4 | 2788 | 0x2788 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 84
174 | 175 | 4x0175 | 3 | N/A | 0x0010 | 4 | 5 | 2789 | 0x2789 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 85
174 | 175 | 4x0175 | 3 | N/A | 0x0020 | 5 | 6 | 2790 | 0x2790 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 86
174 | 175 | 4x0175 | 3 | N/A | 0x0040 | 6 | 7 | 2791 | 0x2791 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 87
174 | 175 | 4x0175 | 3 | N/A | 0x0080 | 7 | 8 | 2792 | 0x2792 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 88
174 | 175 | 4x0175 | 3 | N/A | 0x0100 | 8 | 9 | 2793 | 0x2793 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 89
174 | 175 | 4x0175 | 3 | N/A | 0x0200 | 9 | 10 | 2794 | 0x2794 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 90
174 | 175 | 4x0175 | 3 | N/A | 0x0400 | 10 | 11 | 2795 | 0x2795 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 91
174 | 175 | 4x0175 | 3 | N/A | 0x0800 | 11 | 12 | 2796 | 0x2796 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 92
174 | 175 | 4x0175 | 3 | N/A | 0x1000 | 12 | 13 | 2797 | 0x2797 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 93
174 | 175 | 4x0175 | 3 | N/A | 0x2000 | 13 | 14 | 2798 | 0x2798 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 94
174 | 175 | 4x0175 | 3 | N/A | 0x4000 | 14 | 15 | 2799 | 0x2799 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 95
174 | 175 | 4x0175 | 3 | N/A | 0x8000 | 15 | 16 | 2800 | 0x2800 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 96
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
175 | 176 | 4x0176 | 3 | N/A | 0x0001 | 0 | 1 | 2801 | 0x2801 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 97
175 | 176 | 4x0176 | 3 | N/A | 0x0002 | 1 | 2 | 2802 | 0x2802 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 98
175 | 176 | 4x0176 | 3 | N/A | 0x0004 | 2 | 3 | 2803 | 0x2803 | 1 | N/A | 1.21- | Bit shows fire status for fire cell. Set bit=fire | 99
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
176 | 177 | 4x0177 | 3 | 6 | 0x0001 | 0 | 1 | 2817 | 0x2817 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 1
176 | 177 | 4x0177 | 3 | 6 | 0x0002 | 1 | 2 | 2818 | 0x2818 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 2
176 | 177 | 4x0177 | 3 | 6 | 0x0004 | 2 | 3 | 2819 | 0x2819 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 3
176 | 177 | 4x0177 | 3 | 6 | 0x0008 | 3 | 4 | 2820 | 0x2820 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 4
176 | 177 | 4x0177 | 3 | 6 | 0x0010 | 4 | 5 | 2821 | 0x2821 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 5
176 | 177 | 4x0177 | 3 | 6 | 0x0020 | 5 | 6 | 2822 | 0x2822 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 6
176 | 177 | 4x0177 | 3 | 6 | 0x0040 | 6 | 7 | 2823 | 0x2823 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 7
176 | 177 | 4x0177 | 3 | 6 | 0x0080 | 7 | 8 | 2824 | 0x2824 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 8
176 | 177 | 4x0177 | 3 | 6 | 0x0100 | 8 | 9 | 2825 | 0x2825 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 9
176 | 177 | 4x0177 | 3 | 6 | 0x0200 | 9 | 10 | 2826 | 0x2826 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 10
176 | 177 | 4x0177 | 3 | 6 | 0x0400 | 10 | 11 | 2827 | 0x2827 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 11
176 | 177 | 4x0177 | 3 | 6 | 0x0800 | 11 | 12 | 2828 | 0x2828 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 12
176 | 177 | 4x0177 | 3 | 6 | 0x1000 | 12 | 13 | 2829 | 0x2829 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 13
176 | 177 | 4x0177 | 3 | 6 | 0x2000 | 13 | 14 | 2830 | 0x2830 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 14
176 | 177 | 4x0177 | 3 | 6 | 0x4000 | 14 | 15 | 2831 | 0x2831 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 15
176 | 177 | 4x0177 | 3 | 6 | 0x8000 | 15 | 16 | 2832 | 0x2832 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 16
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
177 | 178 | 4x0178 | 3 | 6 | 0x0001 | 0 | 1 | 2833 | 0x2833 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 17
177 | 178 | 4x0178 | 3 | 6 | 0x0002 | 1 | 2 | 2834 | 0x2834 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 18
177 | 178 | 4x0178 | 3 | 6 | 0x0004 | 2 | 3 | 2835 | 0x2835 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 19
177 | 178 | 4x0178 | 3 | 6 | 0x0008 | 3 | 4 | 2836 | 0x2836 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 20
177 | 178 | 4x0178 | 3 | 6 | 0x0010 | 4 | 5 | 2837 | 0x2837 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 21
177 | 178 | 4x0178 | 3 | 6 | 0x0020 | 5 | 6 | 2838 | 0x2838 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 22
177 | 178 | 4x0178 | 3 | 6 | 0x0040 | 6 | 7 | 2839 | 0x2839 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 23
177 | 178 | 4x0178 | 3 | 6 | 0x0080 | 7 | 8 | 2840 | 0x2840 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 24
177 | 178 | 4x0178 | 3 | 6 | 0x0100 | 8 | 9 | 2841 | 0x2841 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 25
177 | 178 | 4x0178 | 3 | 6 | 0x0200 | 9 | 10 | 2842 | 0x2842 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 26
177 | 178 | 4x0178 | 3 | 6 | 0x0400 | 10 | 11 | 2843 | 0x2843 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 27
177 | 178 | 4x0178 | 3 | 6 | 0x0800 | 11 | 12 | 2844 | 0x2844 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 28
177 | 178 | 4x0178 | 3 | 6 | 0x1000 | 12 | 13 | 2845 | 0x2845 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 29
177 | 178 | 4x0178 | 3 | 6 | 0x2000 | 13 | 14 | 2846 | 0x2846 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 30
177 | 178 | 4x0178 | 3 | 6 | 0x4000 | 14 | 15 | 2847 | 0x2847 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 31
177 | 178 | 4x0178 | 3 | 6 | 0x8000 | 15 | 16 | 2848 | 0x2848 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 32
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
178 | 179 | 4x0179 | 3 | 6 | 0x0001 | 0 | 1 | 2849 | 0x2849 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 33
178 | 179 | 4x0179 | 3 | 6 | 0x0002 | 1 | 2 | 2850 | 0x2850 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 34
178 | 179 | 4x0179 | 3 | 6 | 0x0004 | 2 | 3 | 2851 | 0x2851 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 35
178 | 179 | 4x0179 | 3 | 6 | 0x0008 | 3 | 4 | 2852 | 0x2852 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 36
178 | 179 | 4x0179 | 3 | 6 | 0x0010 | 4 | 5 | 2853 | 0x2853 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 37
178 | 179 | 4x0179 | 3 | 6 | 0x0020 | 5 | 6 | 2854 | 0x2854 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 38
178 | 179 | 4x0179 | 3 | 6 | 0x0040 | 6 | 7 | 2855 | 0x2855 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 39
178 | 179 | 4x0179 | 3 | 6 | 0x0080 | 7 | 8 | 2856 | 0x2856 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 40
178 | 179 | 4x0179 | 3 | 6 | 0x0100 | 8 | 9 | 2857 | 0x2857 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 41
178 | 179 | 4x0179 | 3 | 6 | 0x0200 | 9 | 10 | 2858 | 0x2858 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 42
178 | 179 | 4x0179 | 3 | 6 | 0x0400 | 10 | 11 | 2859 | 0x2859 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 43
178 | 179 | 4x0179 | 3 | 6 | 0x0800 | 11 | 12 | 2860 | 0x2860 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 44
178 | 179 | 4x0179 | 3 | 6 | 0x1000 | 12 | 13 | 2861 | 0x2861 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 45
178 | 179 | 4x0179 | 3 | 6 | 0x2000 | 13 | 14 | 2862 | 0x2862 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 46
178 | 179 | 4x0179 | 3 | 6 | 0x4000 | 14 | 15 | 2863 | 0x2863 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 47
178 | 179 | 4x0179 | 3 | 6 | 0x8000 | 15 | 16 | 2864 | 0x2864 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 48
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
179 | 180 | 4x0180 | 3 | 6 | 0x0001 | 0 | 1 | 2865 | 0x2865 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 49
179 | 180 | 4x0180 | 3 | 6 | 0x0002 | 1 | 2 | 2866 | 0x2866 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 50
179 | 180 | 4x0180 | 3 | 6 | 0x0004 | 2 | 3 | 2867 | 0x2867 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 51
179 | 180 | 4x0180 | 3 | 6 | 0x0008 | 3 | 4 | 2868 | 0x2868 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 52
179 | 180 | 4x0180 | 3 | 6 | 0x0010 | 4 | 5 | 2869 | 0x2869 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 53
179 | 180 | 4x0180 | 3 | 6 | 0x0020 | 5 | 6 | 2870 | 0x2870 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 54
179 | 180 | 4x0180 | 3 | 6 | 0x0040 | 6 | 7 | 2871 | 0x2871 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 55
179 | 180 | 4x0180 | 3 | 6 | 0x0080 | 7 | 8 | 2872 | 0x2872 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 56
179 | 180 | 4x0180 | 3 | 6 | 0x0100 | 8 | 9 | 2873 | 0x2873 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 57
179 | 180 | 4x0180 | 3 | 6 | 0x0200 | 9 | 10 | 2874 | 0x2874 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 58
179 | 180 | 4x0180 | 3 | 6 | 0x0400 | 10 | 11 | 2875 | 0x2875 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 59
179 | 180 | 4x0180 | 3 | 6 | 0x0800 | 11 | 12 | 2876 | 0x2876 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 60
179 | 180 | 4x0180 | 3 | 6 | 0x1000 | 12 | 13 | 2877 | 0x2877 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 61
179 | 180 | 4x0180 | 3 | 6 | 0x2000 | 13 | 14 | 2878 | 0x2878 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 62
179 | 180 | 4x0180 | 3 | 6 | 0x4000 | 14 | 15 | 2879 | 0x2879 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 63
179 | 180 | 4x0180 | 3 | 6 | 0x8000 | 15 | 16 | 2880 | 0x2880 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 64
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
180 | 181 | 4x0181 | 3 | 6 | 0x0001 | 0 | 1 | 2881 | 0x2881 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 65
180 | 181 | 4x0181 | 3 | 6 | 0x0002 | 1 | 2 | 2882 | 0x2882 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 66
180 | 181 | 4x0181 | 3 | 6 | 0x0004 | 2 | 3 | 2883 | 0x2883 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 67
180 | 181 | 4x0181 | 3 | 6 | 0x0008 | 3 | 4 | 2884 | 0x2884 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 68
180 | 181 | 4x0181 | 3 | 6 | 0x0010 | 4 | 5 | 2885 | 0x2885 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 69
180 | 181 | 4x0181 | 3 | 6 | 0x0020 | 5 | 6 | 2886 | 0x2886 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 70
180 | 181 | 4x0181 | 3 | 6 | 0x0040 | 6 | 7 | 2887 | 0x2887 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 71
180 | 181 | 4x0181 | 3 | 6 | 0x0080 | 7 | 8 | 2888 | 0x2888 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 72
180 | 181 | 4x0181 | 3 | 6 | 0x0100 | 8 | 9 | 2889 | 0x2889 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 73
180 | 181 | 4x0181 | 3 | 6 | 0x0200 | 9 | 10 | 2890 | 0x2890 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 74
180 | 181 | 4x0181 | 3 | 6 | 0x0400 | 10 | 11 | 2891 | 0x2891 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 75
180 | 181 | 4x0181 | 3 | 6 | 0x0800 | 11 | 12 | 2892 | 0x2892 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 76
180 | 181 | 4x0181 | 3 | 6 | 0x1000 | 12 | 13 | 2893 | 0x2893 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 77
180 | 181 | 4x0181 | 3 | 6 | 0x2000 | 13 | 14 | 2894 | 0x2894 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 78
180 | 181 | 4x0181 | 3 | 6 | 0x4000 | 14 | 15 | 2895 | 0x2895 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 79
180 | 181 | 4x0181 | 3 | 6 | 0x8000 | 15 | 16 | 2896 | 0x2896 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 80
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
181 | 182 | 4x0182 | 3 | 6 | 0x0001 | 0 | 1 | 2897 | 0x2897 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 81
181 | 182 | 4x0182 | 3 | 6 | 0x0002 | 1 | 2 | 2898 | 0x2898 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 82
181 | 182 | 4x0182 | 3 | 6 | 0x0004 | 2 | 3 | 2899 | 0x2899 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 83
181 | 182 | 4x0182 | 3 | 6 | 0x0008 | 3 | 4 | 2900 | 0x2900 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 84
181 | 182 | 4x0182 | 3 | 6 | 0x0010 | 4 | 5 | 2901 | 0x2901 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 85
181 | 182 | 4x0182 | 3 | 6 | 0x0020 | 5 | 6 | 2902 | 0x2902 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 86
181 | 182 | 4x0182 | 3 | 6 | 0x0040 | 6 | 7 | 2903 | 0x2903 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 87
181 | 182 | 4x0182 | 3 | 6 | 0x0080 | 7 | 8 | 2904 | 0x2904 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 88
181 | 182 | 4x0182 | 3 | 6 | 0x0100 | 8 | 9 | 2905 | 0x2905 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 89
181 | 182 | 4x0182 | 3 | 6 | 0x0200 | 9 | 10 | 2906 | 0x2906 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 90
181 | 182 | 4x0182 | 3 | 6 | 0x0400 | 10 | 11 | 2907 | 0x2907 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 91
181 | 182 | 4x0182 | 3 | 6 | 0x0800 | 11 | 12 | 2908 | 0x2908 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 92
181 | 182 | 4x0182 | 3 | 6 | 0x1000 | 12 | 13 | 2909 | 0x2909 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 93
181 | 182 | 4x0182 | 3 | 6 | 0x2000 | 13 | 14 | 2910 | 0x2910 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 94
181 | 182 | 4x0182 | 3 | 6 | 0x4000 | 14 | 15 | 2911 | 0x2911 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 95
181 | 182 | 4x0182 | 3 | 6 | 0x8000 | 15 | 16 | 2912 | 0x2912 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 96
Register 0-base | Register 1-base | Modicon notation reg. read/write | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read/write | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
182 | 183 | 4x0183 | 3 | 6 | 0x0001 | 0 | 1 | 2913 | 0x2913 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 97
182 | 183 | 4x0183 | 3 | 6 | 0x0002 | 1 | 2 | 2914 | 0x2914 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 98
182 | 183 | 4x0183 | 3 | 6 | 0x0004 | 2 | 3 | 2915 | 0x2915 | 1 | 5 | 1.32- | Activate exercise in fire cell. Set bit=exercise. Automatic clear | 99
Note: Sum alarm is communication error, damper failure or smoke detector service alarm
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
183 | 184 | 4x0184 | 3 | N/A | 0x0001 | 0 | 1 | 2929 | 0x2929 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 1
183 | 184 | 4x0184 | 3 | N/A | 0x0002 | 1 | 2 | 2930 | 0x2930 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 2
183 | 184 | 4x0184 | 3 | N/A | 0x0004 | 2 | 3 | 2931 | 0x2931 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 3
183 | 184 | 4x0184 | 3 | N/A | 0x0008 | 3 | 4 | 2932 | 0x2932 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 4
183 | 184 | 4x0184 | 3 | N/A | 0x0010 | 4 | 5 | 2933 | 0x2933 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 5
183 | 184 | 4x0184 | 3 | N/A | 0x0020 | 5 | 6 | 2934 | 0x2934 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 6
183 | 184 | 4x0184 | 3 | N/A | 0x0040 | 6 | 7 | 2935 | 0x2935 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 7
183 | 184 | 4x0184 | 3 | N/A | 0x0080 | 7 | 8 | 2936 | 0x2936 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 8
183 | 184 | 4x0184 | 3 | N/A | 0x0100 | 8 | 9 | 2937 | 0x2937 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 9
183 | 184 | 4x0184 | 3 | N/A | 0x0200 | 9 | 10 | 2938 | 0x2938 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 10
183 | 184 | 4x0184 | 3 | N/A | 0x0400 | 10 | 11 | 2939 | 0x2939 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 11
183 | 184 | 4x0184 | 3 | N/A | 0x0800 | 11 | 12 | 2940 | 0x2940 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 12
183 | 184 | 4x0184 | 3 | N/A | 0x1000 | 12 | 13 | 2941 | 0x2941 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 13
183 | 184 | 4x0184 | 3 | N/A | 0x2000 | 13 | 14 | 2942 | 0x2942 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 14
183 | 184 | 4x0184 | 3 | N/A | 0x4000 | 14 | 15 | 2943 | 0x2943 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 15
183 | 184 | 4x0184 | 3 | N/A | 0x8000 | 15 | 16 | 2944 | 0x2944 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 16
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
184 | 185 | 4x0185 | 3 | N/A | 0x0001 | 0 | 1 | 2945 | 0x2945 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 17
184 | 185 | 4x0185 | 3 | N/A | 0x0002 | 1 | 2 | 2946 | 0x2946 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 18
184 | 185 | 4x0185 | 3 | N/A | 0x0004 | 2 | 3 | 2947 | 0x2947 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 19
184 | 185 | 4x0185 | 3 | N/A | 0x0008 | 3 | 4 | 2948 | 0x2948 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 20
184 | 185 | 4x0185 | 3 | N/A | 0x0010 | 4 | 5 | 2949 | 0x2949 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 21
184 | 185 | 4x0185 | 3 | N/A | 0x0020 | 5 | 6 | 2950 | 0x2950 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 22
184 | 185 | 4x0185 | 3 | N/A | 0x0040 | 6 | 7 | 2951 | 0x2951 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 23
184 | 185 | 4x0185 | 3 | N/A | 0x0080 | 7 | 8 | 2952 | 0x2952 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 24
184 | 185 | 4x0185 | 3 | N/A | 0x0100 | 8 | 9 | 2953 | 0x2953 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 25
184 | 185 | 4x0185 | 3 | N/A | 0x0200 | 9 | 10 | 2954 | 0x2954 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 26
184 | 185 | 4x0185 | 3 | N/A | 0x0400 | 10 | 11 | 2955 | 0x2955 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 27
184 | 185 | 4x0185 | 3 | N/A | 0x0800 | 11 | 12 | 2956 | 0x2956 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 28
184 | 185 | 4x0185 | 3 | N/A | 0x1000 | 12 | 13 | 2957 | 0x2957 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 29
184 | 185 | 4x0185 | 3 | N/A | 0x2000 | 13 | 14 | 2958 | 0x2958 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 30
184 | 185 | 4x0185 | 3 | N/A | 0x4000 | 14 | 15 | 2959 | 0x2959 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 31
184 | 185 | 4x0185 | 3 | N/A | 0x8000 | 15 | 16 | 2960 | 0x2960 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 32
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
185 | 186 | 4x0186 | 3 | N/A | 0x0001 | 0 | 1 | 2961 | 0x2961 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 33
185 | 186 | 4x0186 | 3 | N/A | 0x0002 | 1 | 2 | 2962 | 0x2962 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 34
185 | 186 | 4x0186 | 3 | N/A | 0x0004 | 2 | 3 | 2963 | 0x2963 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 35
185 | 186 | 4x0186 | 3 | N/A | 0x0008 | 3 | 4 | 2964 | 0x2964 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 36
185 | 186 | 4x0186 | 3 | N/A | 0x0010 | 4 | 5 | 2965 | 0x2965 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 37
185 | 186 | 4x0186 | 3 | N/A | 0x0020 | 5 | 6 | 2966 | 0x2966 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 38
185 | 186 | 4x0186 | 3 | N/A | 0x0040 | 6 | 7 | 2967 | 0x2967 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 39
185 | 186 | 4x0186 | 3 | N/A | 0x0080 | 7 | 8 | 2968 | 0x2968 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 40
185 | 186 | 4x0186 | 3 | N/A | 0x0100 | 8 | 9 | 2969 | 0x2969 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 41
185 | 186 | 4x0186 | 3 | N/A | 0x0200 | 9 | 10 | 2970 | 0x2970 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 42
185 | 186 | 4x0186 | 3 | N/A | 0x0400 | 10 | 11 | 2971 | 0x2971 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 43
185 | 186 | 4x0186 | 3 | N/A | 0x0800 | 11 | 12 | 2972 | 0x2972 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 44
185 | 186 | 4x0186 | 3 | N/A | 0x1000 | 12 | 13 | 2973 | 0x2973 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 45
185 | 186 | 4x0186 | 3 | N/A | 0x2000 | 13 | 14 | 2974 | 0x2974 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 46
185 | 186 | 4x0186 | 3 | N/A | 0x4000 | 14 | 15 | 2975 | 0x2975 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 47
185 | 186 | 4x0186 | 3 | N/A | 0x8000 | 15 | 16 | 2976 | 0x2976 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 48
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
186 | 187 | 4x0187 | 3 | N/A | 0x0001 | 0 | 1 | 2977 | 0x2977 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 49
186 | 187 | 4x0187 | 3 | N/A | 0x0002 | 1 | 2 | 2978 | 0x2978 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 50
186 | 187 | 4x0187 | 3 | N/A | 0x0004 | 2 | 3 | 2979 | 0x2979 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 51
186 | 187 | 4x0187 | 3 | N/A | 0x0008 | 3 | 4 | 2980 | 0x2980 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 52
186 | 187 | 4x0187 | 3 | N/A | 0x0010 | 4 | 5 | 2981 | 0x2981 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 53
186 | 187 | 4x0187 | 3 | N/A | 0x0020 | 5 | 6 | 2982 | 0x2982 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 54
186 | 187 | 4x0187 | 3 | N/A | 0x0040 | 6 | 7 | 2983 | 0x2983 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 55
186 | 187 | 4x0187 | 3 | N/A | 0x0080 | 7 | 8 | 2984 | 0x2984 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 56
186 | 187 | 4x0187 | 3 | N/A | 0x0100 | 8 | 9 | 2985 | 0x2985 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 57
186 | 187 | 4x0187 | 3 | N/A | 0x0200 | 9 | 10 | 2986 | 0x2986 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 58
186 | 187 | 4x0187 | 3 | N/A | 0x0400 | 10 | 11 | 2987 | 0x2987 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 59
186 | 187 | 4x0187 | 3 | N/A | 0x0800 | 11 | 12 | 2988 | 0x2988 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 60
186 | 187 | 4x0187 | 3 | N/A | 0x1000 | 12 | 13 | 2989 | 0x2989 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 61
186 | 187 | 4x0187 | 3 | N/A | 0x2000 | 13 | 14 | 2990 | 0x2990 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 62
186 | 187 | 4x0187 | 3 | N/A | 0x4000 | 14 | 15 | 2991 | 0x2991 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 63
186 | 187 | 4x0187 | 3 | N/A | 0x8000 | 15 | 16 | 2992 | 0x2992 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 64
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
187 | 188 | 4x0188 | 3 | N/A | 0x0001 | 0 | 1 | 2993 | 0x2993 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 65
187 | 188 | 4x0188 | 3 | N/A | 0x0002 | 1 | 2 | 2994 | 0x2994 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 66
187 | 188 | 4x0188 | 3 | N/A | 0x0004 | 2 | 3 | 2995 | 0x2995 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 67
187 | 188 | 4x0188 | 3 | N/A | 0x0008 | 3 | 4 | 2996 | 0x2996 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 68
187 | 188 | 4x0188 | 3 | N/A | 0x0010 | 4 | 5 | 2997 | 0x2997 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 69
187 | 188 | 4x0188 | 3 | N/A | 0x0020 | 5 | 6 | 2998 | 0x2998 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 70
187 | 188 | 4x0188 | 3 | N/A | 0x0040 | 6 | 7 | 2999 | 0x2999 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 71
187 | 188 | 4x0188 | 3 | N/A | 0x0080 | 7 | 8 | 3000 | 0x3000 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 72
187 | 188 | 4x0188 | 3 | N/A | 0x0100 | 8 | 9 | 3001 | 0x3001 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 73
187 | 188 | 4x0188 | 3 | N/A | 0x0200 | 9 | 10 | 3002 | 0x3002 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 74
187 | 188 | 4x0188 | 3 | N/A | 0x0400 | 10 | 11 | 3003 | 0x3003 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 75
187 | 188 | 4x0188 | 3 | N/A | 0x0800 | 11 | 12 | 3004 | 0x3004 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 76
187 | 188 | 4x0188 | 3 | N/A | 0x1000 | 12 | 13 | 3005 | 0x3005 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 77
187 | 188 | 4x0188 | 3 | N/A | 0x2000 | 13 | 14 | 3006 | 0x3006 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 78
187 | 188 | 4x0188 | 3 | N/A | 0x4000 | 14 | 15 | 3007 | 0x3007 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 79
187 | 188 | 4x0188 | 3 | N/A | 0x8000 | 15 | 16 | 3008 | 0x3008 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 80
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
188 | 189 | 4x0189 | 3 | N/A | 0x0001 | 0 | 1 | 3009 | 0x3009 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 81
188 | 189 | 4x0189 | 3 | N/A | 0x0002 | 1 | 2 | 3010 | 0x3010 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 82
188 | 189 | 4x0189 | 3 | N/A | 0x0004 | 2 | 3 | 3011 | 0x3011 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 83
188 | 189 | 4x0189 | 3 | N/A | 0x0008 | 3 | 4 | 3012 | 0x3012 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 84
188 | 189 | 4x0189 | 3 | N/A | 0x0010 | 4 | 5 | 3013 | 0x3013 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 85
188 | 189 | 4x0189 | 3 | N/A | 0x0020 | 5 | 6 | 3014 | 0x3014 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 86
188 | 189 | 4x0189 | 3 | N/A | 0x0040 | 6 | 7 | 3015 | 0x3015 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 87
188 | 189 | 4x0189 | 3 | N/A | 0x0080 | 7 | 8 | 3016 | 0x3016 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 88
188 | 189 | 4x0189 | 3 | N/A | 0x0100 | 8 | 9 | 3017 | 0x3017 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 89
188 | 189 | 4x0189 | 3 | N/A | 0x0200 | 9 | 10 | 3018 | 0x3018 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 90
188 | 189 | 4x0189 | 3 | N/A | 0x0400 | 10 | 11 | 3019 | 0x3019 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 91
188 | 189 | 4x0189 | 3 | N/A | 0x0800 | 11 | 12 | 3020 | 0x3020 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 92
188 | 189 | 4x0189 | 3 | N/A | 0x1000 | 12 | 13 | 3021 | 0x3021 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 93
188 | 189 | 4x0189 | 3 | N/A | 0x2000 | 13 | 14 | 3022 | 0x3022 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 94
188 | 189 | 4x0189 | 3 | N/A | 0x4000 | 14 | 15 | 3023 | 0x3023 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 95
188 | 189 | 4x0189 | 3 | N/A | 0x8000 | 15 | 16 | 3024 | 0x3024 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 96
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
189 | 190 | 4x0190 | 3 | N/A | 0x0001 | 0 | 1 | 3025 | 0x3025 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 97
189 | 190 | 4x0190 | 3 | N/A | 0x0002 | 1 | 2 | 3026 | 0x3026 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 98
189 | 190 | 4x0190 | 3 | N/A | 0x0004 | 2 | 3 | 3027 | 0x3027 | 1 | N/A | 1.33- | Show sum alarm in fire cell. Set bit=alarm | 99
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
190 | 191 | 4x0191 | 3 | N/A | 0x0001 | 0 | 1 | 3041 | 0x3041 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 1
190 | 191 | 4x0191 | 3 | N/A | 0x0002 | 1 | 2 | 3042 | 0x3042 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 2
190 | 191 | 4x0191 | 3 | N/A | 0x0004 | 2 | 3 | 3043 | 0x3043 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 3
190 | 191 | 4x0191 | 3 | N/A | 0x0008 | 3 | 4 | 3044 | 0x3044 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 4
190 | 191 | 4x0191 | 3 | N/A | 0x0010 | 4 | 5 | 3045 | 0x3045 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 5
190 | 191 | 4x0191 | 3 | N/A | 0x0020 | 5 | 6 | 3046 | 0x3046 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 6
190 | 191 | 4x0191 | 3 | N/A | 0x0040 | 6 | 7 | 3047 | 0x3047 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 7
190 | 191 | 4x0191 | 3 | N/A | 0x0080 | 7 | 8 | 3048 | 0x3048 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 8
190 | 191 | 4x0191 | 3 | N/A | 0x0100 | 8 | 9 | 3049 | 0x3049 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 9
190 | 191 | 4x0191 | 3 | N/A | 0x0200 | 9 | 10 | 3050 | 0x3050 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 10
190 | 191 | 4x0191 | 3 | N/A | 0x0400 | 10 | 11 | 3051 | 0x3051 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 11
190 | 191 | 4x0191 | 3 | N/A | 0x0800 | 11 | 12 | 3052 | 0x3052 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 12
190 | 191 | 4x0191 | 3 | N/A | 0x1000 | 12 | 13 | 3053 | 0x3053 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 13
190 | 191 | 4x0191 | 3 | N/A | 0x2000 | 13 | 14 | 3054 | 0x3054 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 14
190 | 191 | 4x0191 | 3 | N/A | 0x4000 | 14 | 15 | 3055 | 0x3055 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 15
190 | 191 | 4x0191 | 3 | N/A | 0x8000 | 15 | 16 | 3056 | 0x3056 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 16
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
191 | 192 | 4x0192 | 3 | N/A | 0x0001 | 0 | 1 | 3057 | 0x3057 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 17
191 | 192 | 4x0192 | 3 | N/A | 0x0002 | 1 | 2 | 3058 | 0x3058 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 18
191 | 192 | 4x0192 | 3 | N/A | 0x0004 | 2 | 3 | 3059 | 0x3059 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 19
191 | 192 | 4x0192 | 3 | N/A | 0x0008 | 3 | 4 | 3060 | 0x3060 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 20
191 | 192 | 4x0192 | 3 | N/A | 0x0010 | 4 | 5 | 3061 | 0x3061 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 21
191 | 192 | 4x0192 | 3 | N/A | 0x0020 | 5 | 6 | 3062 | 0x3062 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 22
191 | 192 | 4x0192 | 3 | N/A | 0x0040 | 6 | 7 | 3063 | 0x3063 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 23
191 | 192 | 4x0192 | 3 | N/A | 0x0080 | 7 | 8 | 3064 | 0x3064 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 24
191 | 192 | 4x0192 | 3 | N/A | 0x0100 | 8 | 9 | 3065 | 0x3065 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 25
191 | 192 | 4x0192 | 3 | N/A | 0x0200 | 9 | 10 | 3066 | 0x3066 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 26
191 | 192 | 4x0192 | 3 | N/A | 0x0400 | 10 | 11 | 3067 | 0x3067 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 27
191 | 192 | 4x0192 | 3 | N/A | 0x0800 | 11 | 12 | 3068 | 0x3068 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 28
191 | 192 | 4x0192 | 3 | N/A | 0x1000 | 12 | 13 | 3069 | 0x3069 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 29
191 | 192 | 4x0192 | 3 | N/A | 0x2000 | 13 | 14 | 3070 | 0x3070 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 30
191 | 192 | 4x0192 | 3 | N/A | 0x4000 | 14 | 15 | 3071 | 0x3071 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 31
191 | 192 | 4x0192 | 3 | N/A | 0x8000 | 15 | 16 | 3072 | 0x3072 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 32
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
192 | 193 | 4x0193 | 3 | N/A | 0x0001 | 0 | 1 | 3073 | 0x3073 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 33
192 | 193 | 4x0193 | 3 | N/A | 0x0002 | 1 | 2 | 3074 | 0x3074 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 34
192 | 193 | 4x0193 | 3 | N/A | 0x0004 | 2 | 3 | 3075 | 0x3075 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 35
192 | 193 | 4x0193 | 3 | N/A | 0x0008 | 3 | 4 | 3076 | 0x3076 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 36
192 | 193 | 4x0193 | 3 | N/A | 0x0010 | 4 | 5 | 3077 | 0x3077 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 37
192 | 193 | 4x0193 | 3 | N/A | 0x0020 | 5 | 6 | 3078 | 0x3078 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 38
192 | 193 | 4x0193 | 3 | N/A | 0x0040 | 6 | 7 | 3079 | 0x3079 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 39
192 | 193 | 4x0193 | 3 | N/A | 0x0080 | 7 | 8 | 3080 | 0x3080 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 40
192 | 193 | 4x0193 | 3 | N/A | 0x0100 | 8 | 9 | 3081 | 0x3081 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 41
192 | 193 | 4x0193 | 3 | N/A | 0x0200 | 9 | 10 | 3082 | 0x3082 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 42
192 | 193 | 4x0193 | 3 | N/A | 0x0400 | 10 | 11 | 3083 | 0x3083 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 43
192 | 193 | 4x0193 | 3 | N/A | 0x0800 | 11 | 12 | 3084 | 0x3084 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 44
192 | 193 | 4x0193 | 3 | N/A | 0x1000 | 12 | 13 | 3085 | 0x3085 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 45
192 | 193 | 4x0193 | 3 | N/A | 0x2000 | 13 | 14 | 3086 | 0x3086 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 46
192 | 193 | 4x0193 | 3 | N/A | 0x4000 | 14 | 15 | 3087 | 0x3087 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 47
192 | 193 | 4x0193 | 3 | N/A | 0x8000 | 15 | 16 | 3088 | 0x3088 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 48
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
193 | 194 | 4x0194 | 3 | N/A | 0x0001 | 0 | 1 | 3089 | 0x3089 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 49
193 | 194 | 4x0194 | 3 | N/A | 0x0002 | 1 | 2 | 3090 | 0x3090 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 50
193 | 194 | 4x0194 | 3 | N/A | 0x0004 | 2 | 3 | 3091 | 0x3091 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 51
193 | 194 | 4x0194 | 3 | N/A | 0x0008 | 3 | 4 | 3092 | 0x3092 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 52
193 | 194 | 4x0194 | 3 | N/A | 0x0010 | 4 | 5 | 3093 | 0x3093 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 53
193 | 194 | 4x0194 | 3 | N/A | 0x0020 | 5 | 6 | 3094 | 0x3094 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 54
193 | 194 | 4x0194 | 3 | N/A | 0x0040 | 6 | 7 | 3095 | 0x3095 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 55
193 | 194 | 4x0194 | 3 | N/A | 0x0080 | 7 | 8 | 3096 | 0x3096 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 56
193 | 194 | 4x0194 | 3 | N/A | 0x0100 | 8 | 9 | 3097 | 0x3097 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 57
193 | 194 | 4x0194 | 3 | N/A | 0x0200 | 9 | 10 | 3098 | 0x3098 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 58
193 | 194 | 4x0194 | 3 | N/A | 0x0400 | 10 | 11 | 3099 | 0x3099 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 59
193 | 194 | 4x0194 | 3 | N/A | 0x0800 | 11 | 12 | 3100 | 0x3100 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 60
193 | 194 | 4x0194 | 3 | N/A | 0x1000 | 12 | 13 | 3101 | 0x3101 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 61
193 | 194 | 4x0194 | 3 | N/A | 0x2000 | 13 | 14 | 3102 | 0x3102 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 62
193 | 194 | 4x0194 | 3 | N/A | 0x4000 | 14 | 15 | 3103 | 0x3103 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 63
193 | 194 | 4x0194 | 3 | N/A | 0x8000 | 15 | 16 | 3104 | 0x3104 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 64
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
194 | 195 | 4x0195 | 3 | N/A | 0x0001 | 0 | 1 | 3105 | 0x3105 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 65
194 | 195 | 4x0195 | 3 | N/A | 0x0002 | 1 | 2 | 3106 | 0x3106 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 66
194 | 195 | 4x0195 | 3 | N/A | 0x0004 | 2 | 3 | 3107 | 0x3107 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 67
194 | 195 | 4x0195 | 3 | N/A | 0x0008 | 3 | 4 | 3108 | 0x3108 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 68
194 | 195 | 4x0195 | 3 | N/A | 0x0010 | 4 | 5 | 3109 | 0x3109 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 69
194 | 195 | 4x0195 | 3 | N/A | 0x0020 | 5 | 6 | 3110 | 0x3110 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 70
194 | 195 | 4x0195 | 3 | N/A | 0x0040 | 6 | 7 | 3111 | 0x3111 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 71
194 | 195 | 4x0195 | 3 | N/A | 0x0080 | 7 | 8 | 3112 | 0x3112 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 72
194 | 195 | 4x0195 | 3 | N/A | 0x0100 | 8 | 9 | 3113 | 0x3113 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 73
194 | 195 | 4x0195 | 3 | N/A | 0x0200 | 9 | 10 | 3114 | 0x3114 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 74
194 | 195 | 4x0195 | 3 | N/A | 0x0400 | 10 | 11 | 3115 | 0x3115 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 75
194 | 195 | 4x0195 | 3 | N/A | 0x0800 | 11 | 12 | 3116 | 0x3116 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 76
194 | 195 | 4x0195 | 3 | N/A | 0x1000 | 12 | 13 | 3117 | 0x3117 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 77
194 | 195 | 4x0195 | 3 | N/A | 0x2000 | 13 | 14 | 3118 | 0x3118 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 78
194 | 195 | 4x0195 | 3 | N/A | 0x4000 | 14 | 15 | 3119 | 0x3119 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 79
194 | 195 | 4x0195 | 3 | N/A | 0x8000 | 15 | 16 | 3120 | 0x3120 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 80
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
195 | 196 | 4x0196 | 3 | N/A | 0x0001 | 0 | 1 | 3121 | 0x3121 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 81
195 | 196 | 4x0196 | 3 | N/A | 0x0002 | 1 | 2 | 3122 | 0x3122 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 82
195 | 196 | 4x0196 | 3 | N/A | 0x0004 | 2 | 3 | 3123 | 0x3123 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 83
195 | 196 | 4x0196 | 3 | N/A | 0x0008 | 3 | 4 | 3124 | 0x3124 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 84
195 | 196 | 4x0196 | 3 | N/A | 0x0010 | 4 | 5 | 3125 | 0x3125 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 85
195 | 196 | 4x0196 | 3 | N/A | 0x0020 | 5 | 6 | 3126 | 0x3126 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 86
195 | 196 | 4x0196 | 3 | N/A | 0x0040 | 6 | 7 | 3127 | 0x3127 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 87
195 | 196 | 4x0196 | 3 | N/A | 0x0080 | 7 | 8 | 3128 | 0x3128 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 88
195 | 196 | 4x0196 | 3 | N/A | 0x0100 | 8 | 9 | 3129 | 0x3129 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 89
195 | 196 | 4x0196 | 3 | N/A | 0x0200 | 9 | 10 | 3130 | 0x3130 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 90
195 | 196 | 4x0196 | 3 | N/A | 0x0400 | 10 | 11 | 3131 | 0x3131 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 91
195 | 196 | 4x0196 | 3 | N/A | 0x0800 | 11 | 12 | 3132 | 0x3132 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 92
195 | 196 | 4x0196 | 3 | N/A | 0x1000 | 12 | 13 | 3133 | 0x3133 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 93
195 | 196 | 4x0196 | 3 | N/A | 0x2000 | 13 | 14 | 3134 | 0x3134 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 94
195 | 196 | 4x0196 | 3 | N/A | 0x4000 | 14 | 15 | 3135 | 0x3135 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 95
195 | 196 | 4x0196 | 3 | N/A | 0x8000 | 15 | 16 | 3136 | 0x3136 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 96
Register 0-base | Register 1-base | Modicon notation reg. read | Read reg. func code | Write reg. func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read | Read bit func code | Write bit func code | Firmware version | Function | Fire cell
196 | 197 | 4x0197 | 3 | N/A | 0x0001 | 0 | 1 | 3137 | 0x3137 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 97
196 | 197 | 4x0197 | 3 | N/A | 0x0002 | 1 | 2 | 3138 | 0x3138 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 98
196 | 197 | 4x0197 | 3 | N/A | 0x0004 | 2 | 3 | 3139 | 0x3139 | 1 | N/A | 1.51- | Show exercise status for fire cell. Set bit=at least one damper is exercising | 99

## Status for damper modules
MODBUS TCP REGISTERS IN SX:ACCESS (8EX2:002)
To simplify the Modbus TCP communication handling, the damper module status (register 32, zero-based)
in the damper modules can be read directly from a cache in the EX2-module itself.
Note:If a module is silent then the status register will be read as all-zero bits.
Enter the station address in the yellow field for the corresponding Group Address (0, 61, 62 or 63) below and then the information will be calculated.
Group 0 | Allowable station address range 1-59
Group Address | Station Address | Address 0-base | Register 1-base | Modicon notation reg.read |  | Read reg func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read |  | Read bit func code | Function (for SX:UNO and SX:DUO) | Action/remarks
0 | 1 | 257 | 258 | 4x0 | 258 | 3 | 0x0001 | 0 | 1 | 4113 | 0x | 4113 | 1 | Standby bit (1=Standby)
0 | 1 | 257 | 258 | 4x0 | 258 | 3 | 0x0002 | 1 | 2 | 4114 | 0x | 4114 | 1 | Fire state | Dampers closed (external/internal cause)
0 | 1 | 257 | 258 | 4x0 | 258 | 3 | 0x0004 | 2 | 3 | 4115 | 0x | 4115 | 1 | Smoke detector Loop error | Previous loop / temperature error
0 | 1 | 257 | 258 | 4x0 | 258 | 3 | 0x0008 | 3 | 4 | 4116 | 0x | 4116 | 1 | Damper 1 error
0 | 1 | 257 | 258 | 4x0 | 258 | 3 | 0x0010 | 4 | 5 | 4117 | 0x | 4117 | 1 | Function test state | Set while the local damper(s) exercise
0 | 1 | 257 | 258 | 4x0 | 258 | 3 | 0x0020 | 5 | 6 | 4118 | 0x | 4118 | 1 | Damper 2 error | Modules with two dampers, not SX:UNO
0 | 1 | 257 | 258 | 4x0 | 258 | 3 | 0x0040 | 6 | 7 | 4119 | 0x | 4119 | 1 | Dampers sum error
0 | 1 | 257 | 258 | 4x0 | 258 | 3 | 0x0080 | 7 | 8 | 4120 | 0x | 4120 | 1 | Over temperature (NTC) | Local alarm due to high temperature
0 | 1 | 257 | 258 | 4x0 | 258 | 3 | 0x0100 | 8 | 9 | 4121 | 0x | 4121 | 1 | Damper 1 closed
0 | 1 | 257 | 258 | 4x0 | 258 | 3 | 0x0200 | 9 | 10 | 4122 | 0x | 4122 | 1 | Damper 1 open
0 | 1 | 257 | 258 | 4x0 | 258 | 3 | 0x0400 | 10 | 11 | 4123 | 0x | 4123 | 1 | Damper 2 closed | Modules with two dampers, not SX:UNO
0 | 1 | 257 | 258 | 4x0 | 258 | 3 | 0x0800 | 11 | 12 | 4124 | 0x | 4124 | 1 | Damper 2 open | Modules with two dampers, not SX:UNO
0 | 1 | 257 | 258 | 4x0 | 258 | 3 | 0x1000 | 12 | 13 | 4125 | 0x | 4125 | 1 | Smoke detector normal run
0 | 1 | 257 | 258 | 4x0 | 258 | 3 | 0x2000 | 13 | 14 | 4126 | 0x | 4126 | 1 | Local alarm point state | Local fire (smoke detector) / temperature alarm
0 | 1 | 257 | 258 | 4x0 | 258 | 3 | 0x4000 | 14 | 15 | 4127 | 0x | 4127 | 1 | Smoke detector service alarm | Clean the detector
0 | 1 | 257 | 258 | 4x0 | 258 | 3 | 0x8000 | 15 | 16 | 4128 | 0x | 4128 | 1 | Smoke loop broken | Local smoke detector loop broken. Also sets local fire alarm
Group 61 | Allowable station address range 1-59
Group Address | Station Address | Address 0-base | Register 1-base | Modicon notation reg.read |  | Read reg func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read |  | Read bit func code | Function (for SX:UNO and SX:DUO) | Action/remarks
61 | 1 | 321 | 322 | 4x0 | 322 | 3 | 0x0001 | 0 | 1 | 5137 | 0x | 5137 | 1 | Standby bit (1=Standby)
61 | 1 | 321 | 322 | 4x0 | 322 | 3 | 0x0002 | 1 | 2 | 5138 | 0x | 5138 | 1 | Fire state | Dampers closed (external/internal cause)
61 | 1 | 321 | 322 | 4x0 | 322 | 3 | 0x0004 | 2 | 3 | 5139 | 0x | 5139 | 1 | Smoke detector Loop error | Previous loop / temperature error
61 | 1 | 321 | 322 | 4x0 | 322 | 3 | 0x0008 | 3 | 4 | 5140 | 0x | 5140 | 1 | Damper 1 error
61 | 1 | 321 | 322 | 4x0 | 322 | 3 | 0x0010 | 4 | 5 | 5141 | 0x | 5141 | 1 | Function test state | Set while the local damper(s) exercise
61 | 1 | 321 | 322 | 4x0 | 322 | 3 | 0x0020 | 5 | 6 | 5142 | 0x | 5142 | 1 | Damper 2 error | Modules with two dampers, not SX:UNO
61 | 1 | 321 | 322 | 4x0 | 322 | 3 | 0x0040 | 6 | 7 | 5143 | 0x | 5143 | 1 | Dampers sum error
61 | 1 | 321 | 322 | 4x0 | 322 | 3 | 0x0080 | 7 | 8 | 5144 | 0x | 5144 | 1 | Over temperature (NTC) | Local alarm due to high temperature
61 | 1 | 321 | 322 | 4x0 | 322 | 3 | 0x0100 | 8 | 9 | 5145 | 0x | 5145 | 1 | Damper 1 closed
61 | 1 | 321 | 322 | 4x0 | 322 | 3 | 0x0200 | 9 | 10 | 5146 | 0x | 5146 | 1 | Damper 1 open
61 | 1 | 321 | 322 | 4x0 | 322 | 3 | 0x0400 | 10 | 11 | 5147 | 0x | 5147 | 1 | Damper 2 closed | Modules with two dampers, not SX:UNO
61 | 1 | 321 | 322 | 4x0 | 322 | 3 | 0x0800 | 11 | 12 | 5148 | 0x | 5148 | 1 | Damper 2 open | Modules with two dampers, not SX:UNO
61 | 1 | 321 | 322 | 4x0 | 322 | 3 | 0x1000 | 12 | 13 | 5149 | 0x | 5149 | 1 | Smoke detector normal run
61 | 1 | 321 | 322 | 4x0 | 322 | 3 | 0x2000 | 13 | 14 | 5150 | 0x | 5150 | 1 | Local alarm point state | Local fire (smoke detector) / temperature alarm
61 | 1 | 321 | 322 | 4x0 | 322 | 3 | 0x4000 | 14 | 15 | 5151 | 0x | 5151 | 1 | Smoke detector service alarm | Clean the detector
61 | 1 | 321 | 322 | 4x0 | 322 | 3 | 0x8000 | 15 | 16 | 5152 | 0x | 5152 | 1 | Smoke loop broken | Local smoke detector loop broken. Also sets local fire alarm
Group 62 | Allowable station address range 1-59
Group Address | Station Address | Address 0-base | Register 1-base | Modicon notation reg.read |  | Read reg func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read |  | Read bit func code | Function (for SX:UNO and SX:DUO) | Action/remarks
62 | 1 | 385 | 386 | 4x0 | 386 | 3 | 0x0001 | 0 | 1 | 6161 | 0x | 6161 | 1 | Standby bit (1=Standby)
62 | 1 | 385 | 386 | 4x0 | 386 | 3 | 0x0002 | 1 | 2 | 6162 | 0x | 6162 | 1 | Fire state | Dampers closed (external/internal cause)
62 | 1 | 385 | 386 | 4x0 | 386 | 3 | 0x0004 | 2 | 3 | 6163 | 0x | 6163 | 1 | Smoke detector Loop error | Previous loop / temperature error
62 | 1 | 385 | 386 | 4x0 | 386 | 3 | 0x0008 | 3 | 4 | 6164 | 0x | 6164 | 1 | Damper 1 error
62 | 1 | 385 | 386 | 4x0 | 386 | 3 | 0x0010 | 4 | 5 | 6165 | 0x | 6165 | 1 | Function test state | Set while the local damper(s) exercise
62 | 1 | 385 | 386 | 4x0 | 386 | 3 | 0x0020 | 5 | 6 | 6166 | 0x | 6166 | 1 | Damper 2 error | Modules with two dampers, not SX:UNO
62 | 1 | 385 | 386 | 4x0 | 386 | 3 | 0x0040 | 6 | 7 | 6167 | 0x | 6167 | 1 | Dampers sum error
62 | 1 | 385 | 386 | 4x0 | 386 | 3 | 0x0080 | 7 | 8 | 6168 | 0x | 6168 | 1 | Over temperature (NTC) | Local alarm due to high temperature
62 | 1 | 385 | 386 | 4x0 | 386 | 3 | 0x0100 | 8 | 9 | 6169 | 0x | 6169 | 1 | Damper 1 closed
62 | 1 | 385 | 386 | 4x0 | 386 | 3 | 0x0200 | 9 | 10 | 6170 | 0x | 6170 | 1 | Damper 1 open
62 | 1 | 385 | 386 | 4x0 | 386 | 3 | 0x0400 | 10 | 11 | 6171 | 0x | 6171 | 1 | Damper 2 closed | Modules with two dampers, not SX:UNO
62 | 1 | 385 | 386 | 4x0 | 386 | 3 | 0x0800 | 11 | 12 | 6172 | 0x | 6172 | 1 | Damper 2 open | Modules with two dampers, not SX:UNO
62 | 1 | 385 | 386 | 4x0 | 386 | 3 | 0x1000 | 12 | 13 | 6173 | 0x | 6173 | 1 | Smoke detector normal run
62 | 1 | 385 | 386 | 4x0 | 386 | 3 | 0x2000 | 13 | 14 | 6174 | 0x | 6174 | 1 | Local alarm point state | Local fire (smoke detector) / temperature alarm
62 | 1 | 385 | 386 | 4x0 | 386 | 3 | 0x4000 | 14 | 15 | 6175 | 0x | 6175 | 1 | Smoke detector service alarm | Clean the detector
62 | 1 | 385 | 386 | 4x0 | 386 | 3 | 0x8000 | 15 | 16 | 6176 | 0x | 6176 | 1 | Smoke loop broken | Local smoke detector loop broken. Also sets local fire alarm
Group 63 | Allowable station address range 1-59
Group Address | Station Address | Address 0-base | Register 1-base | Modicon notation reg.read |  | Read reg func code | Bit mask | Bit nr. 0-base | Bit nr. 1-base | Modbus bit no. | Modicon notation bit read |  | Read bit func code | Function (for SX:UNO and SX:DUO) | Action/remarks
63 | 1 | 449 | 450 | 4x0 | 450 | 3 | 0x0001 | 0 | 1 | 7185 | 0x | 7185 | 1 | Standby bit (1=Standby)
63 | 1 | 449 | 450 | 4x0 | 450 | 3 | 0x0002 | 1 | 2 | 7186 | 0x | 7186 | 1 | Fire state | Dampers closed (external/internal cause)
63 | 1 | 449 | 450 | 4x0 | 450 | 3 | 0x0004 | 2 | 3 | 7187 | 0x | 7187 | 1 | Smoke detector Loop error | Previous loop / temperature error
63 | 1 | 449 | 450 | 4x0 | 450 | 3 | 0x0008 | 3 | 4 | 7188 | 0x | 7188 | 1 | Damper 1 error
63 | 1 | 449 | 450 | 4x0 | 450 | 3 | 0x0010 | 4 | 5 | 7189 | 0x | 7189 | 1 | Function test state | Set while the local damper(s) exercise
63 | 1 | 449 | 450 | 4x0 | 450 | 3 | 0x0020 | 5 | 6 | 7190 | 0x | 7190 | 1 | Damper 2 error | Modules with two dampers, not SX:UNO
63 | 1 | 449 | 450 | 4x0 | 450 | 3 | 0x0040 | 6 | 7 | 7191 | 0x | 7191 | 1 | Dampers sum error
63 | 1 | 449 | 450 | 4x0 | 450 | 3 | 0x0080 | 7 | 8 | 7192 | 0x | 7192 | 1 | Over temperature (NTC) | Local alarm due to high temperature
63 | 1 | 449 | 450 | 4x0 | 450 | 3 | 0x0100 | 8 | 9 | 7193 | 0x | 7193 | 1 | Damper 1 closed
63 | 1 | 449 | 450 | 4x0 | 450 | 3 | 0x0200 | 9 | 10 | 7194 | 0x | 7194 | 1 | Damper 1 open
63 | 1 | 449 | 450 | 4x0 | 450 | 3 | 0x0400 | 10 | 11 | 7195 | 0x | 7195 | 1 | Damper 2 closed | Modules with two dampers, not SX:UNO
63 | 1 | 449 | 450 | 4x0 | 450 | 3 | 0x0800 | 11 | 12 | 7196 | 0x | 7196 | 1 | Damper 2 open | Modules with two dampers, not SX:UNO
63 | 1 | 449 | 450 | 4x0 | 450 | 3 | 0x1000 | 12 | 13 | 7197 | 0x | 7197 | 1 | Smoke detector normal run
63 | 1 | 449 | 450 | 4x0 | 450 | 3 | 0x2000 | 13 | 14 | 7198 | 0x | 7198 | 1 | Local alarm point state | Local fire (smoke detector) / temperature alarm
63 | 1 | 449 | 450 | 4x0 | 450 | 3 | 0x4000 | 14 | 15 | 7199 | 0x | 7199 | 1 | Smoke detector service alarm | Clean the detector
63 | 1 | 449 | 450 | 4x0 | 450 | 3 | 0x8000 | 15 | 16 | 7200 | 0x | 7200 | 1 | Smoke loop broken | Local smoke detector loop broken. Also sets local fire alarm