Solvatten

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Source Protection | Safe Transportation | Sedimentation | Filtration | Disinfection | Safe Storage |

# https://s3-us-west-2.amazonaws.com/cawst-hwts-prod/images/prodtech/solvatten%2010.pngWhat is it?

Solvatten is a portable water treatment device that doubles as a solar water heater. Users open Solvatten like a book, pour water into the inner containers, and expose it to sunlight. Fabric filters (35 micron pore size) in the container openings remove larger particles. Heat and ultraviolet radiation from the sun inactivate and kill pathogens.

# Performance

## Microbiological Effectiveness:

|  |  |
| --- | --- |
| Parameter | Effectiveness |
| Bacteria | Very Effective (>99%) |
| Viruses | Very Effective (>99%) |
| Protozoa | Very Effective (>99%) |
| Helminths | Very Effective\* |

\*Assumption based on pathogen size

## Other Parameters

Not effective for turbidity, chemicals, or colour.

## Source Water Requirements

Turbid water should be filtered or settled before using Solvatten.

## Capacity

Treats 10 L at a time. Treatment takes two to six hours, depending on weather conditions.

## Lifespan

According to the manufacturer, Solvatten lasts 7 years on average. Actual lifespan will vary depending on use, care, and source water quality.

# Ease of Use & Acceptability

## Operation & Maintenance

The user opens Solvatten like a book and fills both containers with water. They push the “sun” button to reset the indicator, then place Solvatten in direct sunlight until the face on the indicator turns from red/sad to green/happy. Typically treatment takes two to six hours. The inside of Solvatten should be cleaned occasionally by adding a handful of dry beans, rice, or woolen balls to the unit along with water, then shaking and rinsing.

## Repair & Replacement

Made of durable plastic, Solvatten does not require batteries, chemicals, or other consumables. The fabric prefilters can be replaced with locally-sourced cloth if needed. The whole unit must be replaced if it breaks.

## User Considerations & Preferences

Solvatten works best in areas where there is lots of sunshine. It can be used for short-term storage of treated water. Solvatten doubles as a solar water heater, warming water to up to 75°C. It does not reduce turbidity.

# Feasibility

## Availability

Must be purchased from Solvatten AB; can be purchased online.

## Cost

US$46–93, depending on unit type and size.

## Size & Weight

The 10 L unit is 36 x 47 x 13 cm and weighs approximately 2.7 kg (empty).

# More Information

Details and references: [www.hwts.info/products-technologies/6201ce2b/solvatten](file:///C:\Users\Jill\Documents\CONSULTING\CAWST\00%20-%20PIPELINE\1-factsheet%20and%20knowledgebase%20editing\3-EDITED%20FACT%20SHEETS\batch%202\pass%201\www.hwts.info\products-technologies\6201ce2b\solvatten)