DIVISION 26 00 00					ELECTRICAL

SECTION 26 50 00 				LIGHTING

SECTION 26 56 00 				EXTERIOR LIGHTING

HELIO BOLLARD, SERIES 1200 WITH EMDEDDED SECURITY CORE

Part 1		General

- Summary

  - Section Includes:

    - Helio M40-P1/K8 & M50-P1/K12 Security Bollard, Series 1200, 11.5" diameter column, illuminated

    - Helio M40-P1/K8 & M50-P1/K12 Security Bollard, Series 1200, 11.5" diameter column, non-illuminated

- References

  - ASTM A106 A106M – Standard Specification for Seamless Carbon Steel Pipe for High-Temperature Service – Grade C

- Performance Requirements

  - Bollards must meet minimum level of K8 impact kinetic energy designation as identified by the ASTM Standard Test Method for Vehicle Crash Testing of Perimeter Barriers. Manufacturer must provide documentation confirming that a finite element analysis has been completed for this product. An M40-P1/K8 rating is equivalent to stopping a 15,000 lb. vehicle traveling at 40 mph in less than 1 meter. An M50-P1/K12 rating is equivalent to stopping a 15,000 lb. vehicle traveling at 50 mph in less than 1 meter.

- Submittals

  - Provide submittals in accordance with Section 01 33 00 – Submittal Procedures.

  - Product data: Manufacturer’s standard data sheets on each product to be used, including:

    - Manufacturer’s standard product literature.

    - Shop Drawings.

    - Installation instructions.

    - Maintenance instructions.

  - Submit finish samples for approval.

- Quality Assurance

  - Manufacturer Qualifications:

    - Minimum 15 years experience in the manufacture of outdoor lighting.

    - Provide reference list of at least ten major transportation authorities, municipalities, universities, or

other high-use public environments currently using site products fabricated by the manufacturer.

- Delivery, Storage and Handling

  - Handle products in accordance with manufacturer’s instructions.

  - Store products in manufacturer’s original packaging until ready for installation.

  - Protect products from impacts and abrasion during storage.

- Warranty

  - Provide manufacturer’s standard warranty:

    - Warranty terms: three years from date of invoice against defects in materials and workmanship.

Part 2		Products

- Manufacturer

  - Basis-of-design product: provide bollards based on the product named.

    - Helio M40-P1/K8 & M50-P1/K12 Security Bollard, Series 1200 by Forms+Surfaces

    - Manufacturer Contact:
Forms+Surfaces
1901 William Flynn Highway 
Glenshaw, PA 15116
phone: 800-451-0410

fax: 412-385-4715

email: sales@forms-surfaces.com

website: www.forms-surfaces.com

  - Security Bollards:

    - Materials:

      - Body: Stainless steel.

      - Base: Aluminum.

      - Head Cap: Stainless steel casting.

      - Lens: .118" thick frosted acrylic.

      - LED Driver: Input voltage is 120-277 VAC nominal. Includes constant output current, with over-voltage, short circuit, overload protection, and has forward-phase, reverse-phase, and 0-10V dimming capabilities. Certifications include: IP64 enclosure, and Class 2 rated output (UL8750).

      - LED Light Engine (for illuminated bollards) (Select one option below):

        - 360° Light Distribution:

            - 40W custom LED light engine.

            - Luminaire lumens: 700.

            - Color temperature (Select one color temperature below):

              - 3,000K.

              - 4,000K.

        - 180° Light Distribution:

            - 20W custom LED light engine.

            - Luminaire lumens: 260.

            - Color temperature (Select one color temperature below):

              - 3,000K.

              - 4,000K.

      - Mounting: cast in place extra-heavy wall steel security core with welded cross supports. 72" Security core minimum 36" embed into concrete and minimum 36" internal to bollard.

      - Heavy steel wall security core set in 60" x 60"W x 60"D footer minimum.

    - Finishes:

      - Body and Head Cap:

        - Satin.

        - Polyester powdercoat (Select one option below):

            - Standard Texture/Gloss from Forms+Surfaces Powdercoat Chart.

            - Custom RAL powdercoat color.

    - Dimensions: 40" high x 11.5" diameter.

    - Mounting (Choose one below):

      - M40-P1/K8 Embedded Deep Set Security Core.

      - M50-P1/K12 Embedded Deep Set Security Core.

      - M50-P1/K12 Embedded Shallow Mount Security Core.

      - Embedded security core. Stainless steel mounting hardware sold separately.

Part 3		Execution

  - Examination

- Verify that substrates are stable and capable of supporting the weight of items covered under this section.

- Verify that foundation, applied finishes, and adjacent construction are ready to receive bollards and are level, plumb, and square within tolerances acceptable to manufacturer.

- Verify that required utilities are in correct location and are of correct capacities for specified products.

  - Installation

- Install in accordance with manufacturer's installation instructions.

- Install in conformance to applicable ADA guidelines and End User’s established accessibility policies.

END OF SECTION